- OBJECTIVE:

The purpose of this SOP is to provide a consistent procedure for monitoring and maintaining the appropriate air differential between a cleanroom and its adjacent areas.

- SCOPE:

This SOP applies to all cleanrooms and associated areas within the facility that require pressure differentials for contamination control, such as buffer areas and surrounding environments.

- RESPONSIBILITIES/ACCOUNTABILITIES:

•	QA Personnel: Ensure that daily monitoring is performed and record the data accurately.

•	Engineering Department: Respond to any deviations and take corrective actions.

•	Quality Control/Assurance: Review monitoring records and ensure compliance with established standards.

- ABBREVIATION AND DEFINITIONS

- HVAC - Heating Ventilation Air Conditioning

- Pa- pascal

- PROCEDURES

- Verify the differential pressure gauge is calibrated and in good working condition.

- Confirm the cleanroom and adjacent areas are operating according to their design parameters.

- Take readings of the differential pressure between the cleanroom and adjacent areas.

- Perform the monitoring task at the established frequency, typically twice a day (morning and afternoon).

- Record the measured differential pressure value in the designated logbook.

- Note the date, time, and personnel performing the task.

- A positive pressure differential of at least 5-20 Pa between cleaner and less clean rooms is generally required.

- Specific requirements may vary based on the ISO class and the nature of the process.

- If the measured pressure is outside the acceptable range, immediately inform the Engineering Department.

- Engineering personnel should investigate the cause and implement corrective actions.

- Quality Assurance reviews the recorded data to ensure continuous compliance.

- All personnel responsible for monitoring must be trained on the proper use of the differential pressure gauge, understanding of the acceptance criteria, and the correct procedure for reporting deviations.

Materials, Equipment, Apparatus and Reagents

- Differential Pressure Gauge/Sensor: A calibrated instrument to measure the pressure difference.

- Logbook/Data Sheet: For recording monitoring results.

6.0 REFERENCE AND ENCLOSURE

WHO guidelines

ENCLOSURE 1- PRESSURE DIFFERENTIAL MONITORING LOG

- TRAINING INVOLVEMENT

| All departmental managers | All sectional heads |
| --- | --- |
| QA Doc. Unit staff | All staff |

- DISTRIBUTION AND CONTROL:

| MASTER COPIES | QUALITY ASSURANCE |
| --- | --- |
| CONTROLLED COPIES | ALL DEPARTMENT |

9.0 CHANGE HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| 00 | Nil | First issue |
| 06 | 05 | - Change in sop format. - Inclusion of traceability of enclosures to parent SOP |