- OBJECTIVE:

To lay down a procedure for monitoring temperature, relative humidity and differential pressure in controlled areas.

- SCOPE:

This SOP is applicable for monitoring and recording the temperature (°C), Relative humidity (%) and differential pressure (Pa) in controlled areas using wet and dry bulb or digital hygrometers or by using thermo-hygrometer for temperature and relative humidity and Magnehelic gauge for Differential Pressure in controlled areas of production, Quality Control, Warehouse.

- RESPONSIBILITIES/ACCOUNTABILITIES:

- Personnel of concern department are responsible for monitoring and verification for Temperature, Relative Humidity and Differential Pressure.

- Head-Concerned department is responsible to ensure the prevailing Temperature, Relative Humidity and Differential Pressure is within limits as per SOP.

- Head-Engineering/Head-Q.A shall be accountable for implementation and compliance of SOP

- ABBREVIATION AND DEFINITIONS

- °C : Degree Centigrade

- RH : Relative Humidity

- QA. : Quality Assurance

- Pa : Pascal

- MmH2O: Millimeter of water

- Min : Minimum

- Max: Maximum

- AHU: Air Handling Unit

- 0F: Degree Fahrenheit

- PROCEDURES

- Procedure for Monitoring of Temperature, Relative Humidity by thermo hygrometer and Wet and Dry bulb Hygrometer.

Preparation of the thermo hygrometer or Wet and Dry bulb Hygrometer for Monitoring of Temperature and Relative Humidity.

- Check the calibration status of the instrument.

- Check and ensure that the wick is fixed on the wet bulb thermometer.

- Fill the cistern with purified water at the start of the shift.

- Check and ensure that the wick is wet.

- Check that both the thermometers are fixed properly.

CALIBRATION

  - Take a calibrated thermometer and wrap round the bulb small quantity of cotton wool

  - Immersed the cotton wool in cool clean water

  - Wave the thermometer gently round the area where your hygrometer is placed for 10minutes and take your readings

  - Remove the wet cotton wool and wipe dry the bulb of your thermometer

  - Wave the dry thermometer gently round the area for at least 10 minutes and take your reading

  - Calculate your depression by subtracting the wet reading from the dry reading of your thermometer

  - Check the reading of the Hygrometer placed in the area, any deviation of more than, ±2.0OC for temperature and ±5% for humidity is not acceptable. If any such deviation is observed check if the Hygrometer wet bulb water cup holder is clean

  - Check if the dry bulb is cleaned and not broken

  - Engineering department along with QA shall investigate the reason for deviation in temperature and/or humidity and rectify the same. In case of major breakdown, Final decision should be taken by QA for line of action.

Operation:

- (Zeal type), check the reading directly without swinging. check the reading of wet and dry bulb thermometer in the respective area

- Subtract the reading of the wet bulb from that of dry bulb column and the difference will give the depression value.

- If the instrument show the reading in Fahrenheit (0 F) then convert the Fahrenheit reading in 0C by using formula given below.       O C = (0 F-32/ 9) X 5

- Refer to the Temperature and Humidity chart to locate the readings of dry bulb and the depression value given by the thermo hygrometer. Read the % RH at the intersection of the two columns. In case, values of dry bulb and depression of wet bulb fall as shown in example (b), interpolate the values as given below.

- The following examples illustrate the method of using the table.

    - Dry Bulb …. …. …. 30 °C, Wet Bulb …. …. …. 25 °C

Hence the depression of the Wet Bulb: 30 °C – 25 °C = 5 °C

Reading directly from the tables, the relative humidity is 65 % (intersection value of 30 °C of dry

Bulb and 5 °C of depression value)

    - Dry Bulb …. …. …. 23.5 °C, Wet Bulb …. …. …. 16 °C

The depression of the wet Bulb: 23.5 °C – 16.0 °C=7.5 °C

To find the relative humidity, intersection value of 23.5 °C of dry bulb and 7.5 °C depression of

wet bulb is required.

But 23.5 is not available in Temperature and Humidity chart, so, mean of intersection value of 23

°C of dry bulb and 7.5 °C depression of wet bulb and 24 °C of dry bulb and 7.5 °C depression of

Wet bulb is noted as below

The readings are as follows:

| ###### Dry Bulb (°C) | Depression of Wet Bulb °C = 7.5°C |
| --- | --- |
| 23 | 41 |
| 24 | 43 |

- The mean of two readings i.e. 41 and 43 is 42.Hence the relative humidity is 42%.

- The dry bulb reading indicates the prevailing temperature of the respective area.

- Record the Temperature and Relative Humidity at starting of the shift + 30 min and after every 4 hours ± 30 minutes for production oral, pilot plant, warehouse and 2 hours ± 15 minutes for production injection till completion of the activity or end of shift whichever is later in Format.

- The temperature and relative humidity for all areas shall be maintained.

- If the temperature and/or humidity is not within the limits, discontinue the activity and Inform to QA and Engineering Dept.

- Engineering department along with QA shall investigate the reason for deviation in temperature and/or humidity and rectify the same. In case of major breakdown, Final decision should be taken by QA for line of action.

- Alert limit for temperature is 300C and relative humidity is 68% while the action limit is 320C and RH 70%

Maintenance of Wet and Dry bulb Hygrometer/ Thermo-hygrometer:

  - Ensure that sufficient purified water is available in the cistern.

  - Ensure that the wick is clean and wet.

  - Ensure that the top end of the wick covers the bulb completely. (To ensure, the wick may be fastened or tied to wet bulb).

  - Check and ensure that no scales or deposit are observed on the wick.

  - Hygrometer should be calibrated once in year by external approved party

Precautions to be taken During Handling of Wet and Dry bulb Hygrometer:

  - Ensure that product in the respective area is in closed condition.

  - Ensure the hygrometer is handled carefully.

  - While handling if thermometer got damaged, inform to QA for further action.

  - Clean the broken thermometer in the area and replace immediately with calibrated thermo hygrometer.

Procedure for monitoring of Temperature and Relative Humidity by Digital hygrometer

  - Check the calibration status of the instrument.

  - Check the temperature and relative humidity displayed in the digital hygrometer monitor.

  - Record the Temperature and Relative Humidity at starting of the shift + 30 min and after every 4 hours ± 30 minutes for production (oral), warehouse and 2 hours ± 15 minutes for production (injection) till completion of the activity or end of shift whichever is later.

  - Record the previous day minimum and maximum temperature and relative humidity in the format. Record the minimum and maximum at the time of observing and recording daily initial reading. Recording of minimum and maximum reading.

  - Record the min and max temperature and RH from hygrometer display menu by pressing “MODE” key.

  - Delete the minimum and maximum reading from the memory of hygrometer that is required to leave memory space to record the next day min and max reading.

  - For resetting the minimum value, press “MODE” key for 3 seconds and then press “SET” key, it will reset the min value.

  - For resetting the maximum value, press “MODE” key for 3 seconds and then press “SET” key, it will reset the max value.

Procedure for monitoring of Differential Pressure in Different Areas:

    - AHUs of all areas (Cubicle and adjacent area) should be started 20 to 30 minutes before starting the activity of respective areas.

    - Ensure that the door of the cubicle and adjacent area are in closed condition.

    - Read the value (differential pressure between adjacently located areas) on wall mounted Magnehelic gauge which is directly corresponding to the pointer needle, if the indicator needle rests in between two divisions on the scale, the average of both readings to be considered.

e.g.: Magnehelic gauge

Range: 1.5 to 14.0mmH2O. (1mmH20 Equivalent to 9.80665pa)

  - Record the difference pressure (Magnehelic gauge) at starting the shift + 30 min and after every 3 hours ± 30 minutes till completion of the activity or end of shift.

  - If the temperature and/or humidity is not within the limits, discontinue the activity and Inform to QA and Engineering Dept.

  - Engineering department along with QA shall investigate the reason for deviation in temperature and/or humidity and rectify the same. In case of major breakdown, Final decision should be taken by QA for line of action.

  - Magnehelic gauge should be calibrated once in six months by external approved party.

  - Ensure the tag calibrated is affixed below the Magnehelic. The same shall be verified by QA.

  - If the Temperature, Relative Humidity & Differential Pressure are out of the acceptance criteria, in that case the person monitoring the Temperature, Relative Humidity & Differential Pressure shall inform to Maintenance & QA department for preventive & corrective action.

  - Final decision should be taken by QA for line of action.

  - Alert limit is 1.55mmH20 while action limit is 13.5mmH20

NOTE:  For monitoring and recording the temperature (°C) and Relative humidity (%) in controlled areas either Hygrometers can be used depending on the availability of the instrument.

All the hygrometers shall be placed at the hot spots identified in each room.

- REFERENCE AND ENCLOSURE

ENLCLOSURE 1- Temperature and Relative Humidity monthly Chart- BML-QDG-QA-043-F01

ENLCLOSURE 2- Differential Pressure record Sheet - BML-QDG-QA-043-F02

7.0 TRAINING INVOLVEMENT

| All concerned managers | In-process Officers |
| --- | --- |
| QA Doc. Unit staff | Lab Assistants |

8.0 DISTRIBUTION AND CONTROL:

| MASTER COPIES | QUALITY ASSURANCE |
| --- | --- |
| CONTROLLED COPIES | ALL DEPARTMENT |

9.0 CHANGE HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| 00 | Nil | First issue |
| 06 | 05 | - Change in SOP format. - Inclusion of traceability of enclosures to parent SOP |