LOCATION – INFUSION STORES

DOC. NO. – BML/QDF/QA/TMR/001

PROVIDED BY:

BIOMEDICAL LIMTED

KWARA STATE, NIGERIA

BIOMEDICAL LIMITED

# TEMPERATURE MAPPING

INFUSION STORES

Contents

APPROVAL	3

INTRODUCTION	4

TEMPERATURE MAPPING STUDY OVERVIEW	5

DATA COLLECTION GUIDE	6

SPATIAL MAP	7

TEMPERATURE/HUMIDITY MAPPING DATA	9

APPROVED FINISHED GOODS STORE: AUGUST 2025	9

QUARANTINE FINISHED GOODS STORE: AUGUST 2025	11

PACKAGING MATERIAL STORE: AUGUST 2025	13

APPROVED RAW MATERIAL STORE: AUGUST 2025	15

QUARANTINED RAW MATERIAL STORE: AUGUST 2025	17

SUMMARY OF DATA	19

DISCUSSION OF DATA	20

CONCLUSION	20

RECOMMENDATION	20

ATTACHMENT	21

APPROVAL

|  | WRITTEN: | REVIEWED: |
| --- | --- | --- |
| Signature: |  |  |
| Position: |  |  |
| Date: |  |  |

|  | APPROVED | AUTHORISED |
| --- | --- | --- |
| Signature: |  |  |
| Position: |  |  |
| Date: |  |  |

# INTRODUCTION

This mapping study document explains how conditions change in the store and its suitability for its use. The study determines where hot and cold spots appear and proffers recommendations for continuous use of the storage area.

The mapping exercise of the storage areas will ensure that the company will understand its storage area and identify any potential areas therein that may be unsuitable for storing materials/medicines.

The study results are included in this report and observing the standard operating procedure (BML/QDG/QA/043) in mind against overall regulatory requirements for the storage of drug substances, intermediates, and products.

# TEMPERATURE MAPPING STUDY OVERVIEW

| Company and Location | BIOMEDICAL LIMITED 1, Ohimege Road, Gaa-Imam Industrial Estate, Ilorin. Kwara state |
| --- | --- |
| Facility | Infusion plant: Raw Material Store Packaging Material Store Finished Goods Store (Quarantine and Approved) |
| Raining season / Dry season | Wet |
| Temperature/Relative Humidity Type | See Protocol for Calibration of Thermohygrometers Analogue Thermohygrometer BL/THM/THA/xxx |
| Number of Devices Used | Approved Raw Materials Store (ARMS) – 8, Quarantine Raw Material Store (QRMS) – 5 Quarantine Finished Goods Store (QFGS) – 8, Approved Finished Goods Store (AFGS) – 8, Packaging Material Store (PMS) - 6 |
| Device Position | Corners and spatial centers |
| Date mapping started | 11/08/2025 |
| Date mapping Ended | 17/08/2025 |
| Required Range | Temperature, T: not more than 32oC, Humidity, H: not more than 75% |
| Alert Limit | T:30oC, H: 68% |
| Action limit | T:32oC, H:70% |

TEMPERATURE/RELATIVE HUMIDITY SPECIFICATION

| Temperature/Relative Humidity Type | Analogue thermohygrometer |
| --- | --- |
| Thermohygrometer bandwidth | T:1oC, H:1% |
| Recording Interval | 2 Hours |
| Temperature Range | Not more than 32oC |
| Relative Humidity Range | Not More Than 75% |

# DATA COLLECTION GUIDE

Data shall be collected for the raw material store, packaging material store, bottle room, approved finished goods store, and cold room. Data collected shall be statistically treated and discussed, and recommendations shall be proffered when the need arises. Data collected shall be for seven consecutive days, including five work-days and two weekend days in the season. All values of Temperature (T) and Relative Humidity (H) have units C and % respectively.

Collection Schedule:

Dry season (December to March): January & February

Raining season (April to November): August & September

# SPATIAL MAP

QUARANTINVE AND APPROVED FINISHED GOODS STORE SPATIAL POSITIONING OF SENSORS

1	2

Entrance

7

3	                                               4

8

Entrance

5                                      	6

1                                                             					   2

4

3 									5

PACKAGING MATERIAL STORE SPATIAL POSITIONING OF SENSORS

RAW MATERIAL STORE SPATIAL POSITIONING OF SENSORS

Approved RM                                                                       Quarantine

1                                        2                                            3               1                          2

4                                              5                                                3

6                                    7                                                      8            4                            5

# TEMPERATURE/HUMIDITY MAPPING DATA

## APPROVED FINISHED GOODS STORE: AUGUST 2025

| S/N | DATE | TIME | DEPT | READINGS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MEAN |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  |  |  |  |
|  |  |  |  | T | H | T | H | T | H | T | H | T | H | T | H | T | H | T | H | T |  | H |
| 1 | 11/08/2025 | 9:00 AM | AFGS | 23 | 63 | 22 | 64 | 23 | 62 | 22 | 65 | 21 | 64 | 22 | 63 | 23 | 64 | 22 | 62 | 22.25 |  | 63.38 |
|  |  | 11:00 AM | AFGS | 25 | 60 | 26 | 61 | 24 | 62 | 25 | 60 | 25 | 61 | 24 | 62 | 26 | 60 | 25 | 61 | 25 |  | 60.88 |
|  |  | 1:00 PM | AFGS | 27 | 58 | 28 | 59 | 27 | 57 | 26 | 58 | 26 | 57 | 27 | 58 | 26 | 57 | 27 | 56 | 26.75 |  | 57.5 |
|  |  | 3:00 PM | AFGS | 29 | 55 | 28 | 56 | 29 | 54 | 28 | 55 | 27 | 54 | 28 | 55 | 28 | 53 | 29 | 54 | 28.25 |  | 54.5 |
| 2 | 12/08/2025 | 9:00 AM | AFGS | 22 | 64 | 23 | 65 | 22 | 64 | 23 | 63 | 22 | 65 | 24 | 64 | 23 | 66 | 22 | 64 | 22.63 |  | 64.38 |
|  |  | 11:00 AM | AFGS | 24 | 61 | 25 | 60 | 24 | 62 | 25 | 61 | 26 | 60 | 25 | 61 | 24 | 62 | 25 | 60 | 24.75 |  | 60.88 |
|  |  | 1:00 PM | AFGS | 27 | 58 | 26 | 59 | 27 | 57 | 26 | 58 | 27 | 57 | 26 | 58 | 27 | 56 | 26 | 58 | 26.5 |  | 57.63 |
|  |  | 3:00 PM | AFGS | 29 | 54 | 28 | 55 | 27 | 56 | 28 | 54 | 29 | 53 | 28 | 54 | 29 | 55 | 28 | 54 | 28.25 |  | 54.38 |
| 3 | 13/08/2025 | 9:00 AM | AFGS | 23 | 64 | 22 | 63 | 23 | 65 | 22 | 64 | 21 | 66 | 23 | 64 | 22 | 65 | 22 | 63 | 22.25 |  | 64.25 |
|  |  | 11:00 AM | AFGS | 25 | 61 | 26 | 62 | 25 | 63 | 26 | 62 | 25 | 63 | 24 | 61 | 26 | 62 | 25 | 61 | 25.25 |  | 61.88 |
|  |  | 1:00 PM | AFGS | 27 | 57 | 26 | 58 | 27 | 59 | 26 | 57 | 27 | 58 | 26 | 57 | 27 | 58 | 26 | 57 | 26.5 |  | 57.63 |
|  |  | 3:00 PM | AFGS | 28 | 56 | 29 | 54 | 28 | 55 | 27 | 56 | 29 | 55 | 28 | 54 | 29 | 53 | 28 | 55 | 28.25 |  | 54.75 |
| 4 | 14/08/2025 | 9:00 AM | AFGS | 22 | 65 | 23 | 64 | 22 | 63 | 21 | 64 | 22 | 65 | 23 | 64 | 22 | 63 | 23 | 64 | 22.25 |  | 64 |
|  |  | 11:00 AM | AFGS | 24 | 62 | 25 | 61 | 24 | 62 | 25 | 60 | 26 | 61 | 25 | 62 | 24 | 61 | 25 | 60 | 24.75 |  | 61.13 |
|  |  | 1:00 PM | AFGS | 27 | 59 | 28 | 58 | 27 | 57 | 26 | 58 | 27 | 57 | 28 | 58 | 27 | 56 | 26 | 57 | 27 |  | 57.5 |
|  |  | 3:00 PM | AFGS | 29 | 55 | 28 | 56 | 29 | 54 | 28 | 55 | 27 | 54 | 28 | 55 | 29 | 53 | 28 | 54 | 28.25 |  | 54.5 |
| 5 | 15/08/2025 | 9:00 AM | AFGS | 22 | 63 | 23 | 64 | 22 | 63 | 21 | 62 | 22 | 63 | 23 | 64 | 22 | 63 | 23 | 64 | 22.25 |  | 63.25 |
|  |  | 11:00 AM | AFGS | 24 | 60 | 25 | 61 | 24 | 60 | 23 | 59 | 25 | 60 | 24 | 61 | 25 | 60 | 24 | 61 | 24.25 |  | 60.25 |
|  |  | 1:00 PM | AFGS | 26 | 56 | 27 | 57 | 26 | 58 | 27 | 57 | 26 | 56 | 27 | 57 | 26 | 56 | 27 | 58 | 26.5 |  | 56.88 |
|  |  | 3:00 PM | AFGS | 28 | 54 | 29 | 53 | 28 | 55 | 27 | 54 | 28 | 53 | 27 | 54 | 29 | 52 | 28 | 54 | 28 |  | 53.63 |
| 6 | 16/08/2023 | 9:00 AM | AFGS | 22 | 64 | 21 | 63 | 22 | 63 | 23 | 62 | 23 | 63 | 22 | 64 | 21 | 63 | 22 | 62 | 22 |  | 63 |
|  |  | 11:00 AM | AFGS | 24 | 61 | 25 | 60 | 24 | 61 | 26 | 60 | 25 | 60 | 23 | 62 | 23 | 61 | 24 | 60 | 24.25 |  | 60.63 |
|  |  | 1:00 PM | AFGS | 27 | 57 | 26 | 57 | 27 | 58 | 27 | 57 | 26 | 57 | 25 | 59 | 26 | 58 | 25 | 57 | 26.13 |  | 57.5 |
|  |  | 3:00 PM | AFGS | 28 | 54 | 28 | 55 | 28 | 55 | 29 | 54 | 28 | 55 | 27 | 56 | 27 | 55 | 26 | 54 | 27.63 |  | 54.75 |
| 7 | 17/08/2023 | 9:00 AM | AFGS | 21 | 63 | 22 | 64 | 23 | 62 | 22 | 63 | 22 | 63 | 23 | 62 | 22 | 64 | 23 | 63 | 22.25 |  | 63 |
|  |  | 11:00 AM | AFGS | 24 | 59 | 25 | 62 | 25 | 59 | 24 | 61 | 24 | 60 | 25 | 60 | 25 | 62 | 25 | 61 | 24.63 |  | 60.5 |
|  |  | 1:00 PM | AFGS | 26 | 56 | 26 | 59 | 27 | 57 | 26 | 58 | 26 | 57 | 27 | 57 | 27 | 58 | 27 | 57 | 26.5 |  | 57.38 |
|  |  | 3:00 PM | AFGS | 28 | 54 | 27 | 56 | 28 | 54 | 28 | 55 | 27 | 54 | 29 | 55 | 28 | 56 | 29 | 55 | 28 |  | 54.88 |
| Mean |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.4025 | 59.1007143 |
| MIN |  |  |  | 21 | 54 | 21 | 53 | 22 | 54 | 21 | 54 | 21 | 53 | 22 | 54 | 21 | 52 | 22 | 54 |  |  |  |
| MAX |  |  |  | 29 | 65 | 29 | 65 | 29 | 65 | 29 | 65 | 29 | 66 | 29 | 64 | 29 | 66 | 29 | 64 |  |  |  |

## QUARANTINE FINISHED GOODS STORE: AUGUST 2025

| S/N | DATE | TIME | DEPT | READINGS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MEAN |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  |  |  |  |
|  |  |  |  | T | H | T | H | T | H | T | H | T | H | T | H | T | H | T | H | T |  | H |
| 1 | 11/08/2025 | 9:00 AM | QFGS | 24 | 63 | 22 | 66 | 21 | 64 | 23 | 65 | 22 | 62 | 24 | 64 | 21 | 65 | 23 | 63 | 22.5 |  | 64 |
|  |  | 11:00 AM | QFGS | 23 | 62 | 26 | 60 | 24 | 63 | 25 | 61 | 23 | 62 | 26 | 60 | 24 | 62 | 25 | 61 | 24.5 |  | 61.375 |
|  |  | 1:00 PM | QFGS | 28 | 57 | 25 | 60 | 27 | 58 | 26 | 60 | 28 | 57 | 25 | 59 | 27 | 58 | 26 | 60 | 26.5 |  | 58.625 |
|  |  | 3:00 PM | QFGS | 29 | 55 | 27 | 56 | 30 | 53 | 28 | 56 | 27 | 54 | 29 | 55 | 27 | 56 | 28 | 54 | 28.125 |  | 54.875 |
| 2 | 12/08/2025 | 9:00 AM | QFGS | 23 | 64 | 21 | 66 | 22 | 63 | 24 | 64 | 23 | 62 | 22 | 65 | 24 | 63 | 21 | 64 | 22.5 |  | 63.875 |
|  |  | 11:00 AM | QFGS | 26 | 62 | 23 | 61 | 25 | 63 | 24 | 62 | 26 | 61 | 23 | 60 | 25 | 62 | 24 | 63 | 24.5 |  | 61.75 |
|  |  | 1:00 PM | QFGS | 25 | 59 | 27 | 60 | 26 | 61 | 27 | 58 | 25 | 60 | 27 | 59 | 26 | 60 | 27 | 59 | 26.25 |  | 59.5 |
|  |  | 3:00 PM | QFGS | 28 | 57 | 29 | 55 | 27 | 58 | 30 | 54 | 28 | 57 | 29 | 56 | 27 | 57 | 28 | 55 | 28.25 |  | 56.125 |
| 3 | 13/08/2025 | 9:00 AM | QFGS | 23 | 62 | 22 | 66 | 21 | 64 | 23 | 65 | 22 | 63 | 24 | 64 | 21 | 66 | 22 | 63 | 22.25 |  | 64.125 |
|  |  | 11:00 AM | QFGS | 26 | 61 | 23 | 63 | 25 | 62 | 24 | 61 | 26 | 63 | 24 | 60 | 23 | 62 | 25 | 61 | 24.5 |  | 61.625 |
|  |  | 1:00 PM | QFGS | 27 | 61 | 26 | 59 | 25 | 60 | 27 | 58 | 26 | 61 | 28 | 59 | 25 | 60 | 27 | 58 | 26.375 |  | 59.5 |
|  |  | 3:00 PM | QFGS | 29 | 55 | 28 | 57 | 30 | 54 | 27 | 56 | 28 | 55 | 29 | 57 | 27 | 54 | 28 | 56 | 28.25 |  | 55.5 |
| 4 | 14/08/2025 | 9:00 AM | QFGS | 24 | 62 | 21 | 65 | 22 | 63 | 23 | 64 | 24 | 61 | 22 | 64 | 23 | 62 | 21 | 65 | 22.5 |  | 63.25 |
|  |  | 11:00 AM | QFGS | 25 | 62 | 24 | 61 | 26 | 60 | 23 | 62 | 24 | 63 | 25 | 61 | 24 | 62 | 26 | 60 | 24.625 |  | 61.375 |
|  |  | 1:00 PM | QFGS | 27 | 59 | 26 | 60 | 25 | 58 | 28 | 59 | 26 | 57 | 27 | 58 | 25 | 59 | 26 | 58 | 26.25 |  | 58.5 |
|  |  | 3:00 PM | QFGS | 30 | 54 | 28 | 55 | 27 | 56 | 29 | 54 | 28 | 53 | 27 | 55 | 30 | 54 | 28 | 55 | 28.375 |  | 54.5 |
| 5 | 15/08/2025 | 9:00 AM | QFGS | 23 | 62 | 21 | 64 | 24 | 63 | 22 | 62 | 23 | 63 | 24 | 62 | 21 | 64 | 22 | 63 | 22.5 |  | 62.875 |
|  |  | 11:00 AM | QFGS | 24 | 61 | 26 | 59 | 25 | 60 | 23 | 61 | 24 | 60 | 25 | 61 | 26 | 59 | 23 | 60 | 24.5 |  | 60.125 |
|  |  | 1:00 PM | QFGS | 27 | 56 | 25 | 58 | 26 | 57 | 27 | 59 | 26 | 56 | 25 | 58 | 27 | 57 | 26 | 59 | 26.125 |  | 57.5 |
|  |  | 3:00 PM | QFGS | 28 | 54 | 27 | 56 | 30 | 53 | 28 | 55 | 27 | 54 | 29 | 53 | 28 | 56 | 27 | 55 | 28 |  | 54.5 |
| 6 | 16/08/2025 | 9:00 AM | QFGS | 22 | 64 | 24 | 62 | 21 | 65 | 23 | 63 | 22 | 64 | 21 | 63 | 23 | 62 | 22 | 65 | 22.25 |  | 63.5 |
|  |  | 11:00 AM | QFGS | 25 | 60 | 24 | 62 | 23 | 61 | 26 | 59 | 25 | 60 | 24 | 62 | 23 | 61 | 24 | 60 | 24.25 |  | 60.625 |
|  |  | 1:00 PM | QFGS | 26 | 58 | 27 | 57 | 25 | 59 | 26 | 57 | 27 | 56 | 25 | 58 | 26 | 57 | 27 | 58 | 26.125 |  | 57.5 |
|  |  | 3:00 PM | QFGS | 29 | 54 | 27 | 55 | 28 | 54 | 30 | 53 | 27 | 55 | 28 | 54 | 29 | 53 | 27 | 54 | 28.125 |  | 54 |
| 7 | 17/08/2025 | 9:00 AM | QFGS | 22 | 65 | 23 | 63 | 24 | 62 | 21 | 64 | 23 | 63 | 22 | 62 | 24 | 63 | 21 | 64 | 22.5 |  | 63.25 |
|  |  | 11:00 AM | QFGS | 25 | 60 | 24 | 61 | 23 | 62 | 26 | 59 | 25 | 60 | 24 | 62 | 23 | 61 | 25 | 59 | 24.375 |  | 60.5 |
|  |  | 1:00 PM | QFGS | 26 | 59 | 27 | 57 | 25 | 58 | 26 | 60 | 27 | 56 | 26 | 58 | 25 | 59 | 27 | 57 | 26.125 |  | 58 |
|  |  | 3:00 PM | QFGS | 28 | 56 | 27 | 54 | 29 | 55 | 28 | 57 | 27 | 56 | 29 | 54 | 28 | 55 | 27 | 56 | 27.875 |  | 55.375 |
| Mean |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.3214286 |  | 59.5089286 |
| MIN |  |  |  | 22 | 54 | 21 | 54 | 21 | 53 | 21 | 53 | 22 | 53 | 21 | 53 | 21 | 53 | 21 | 54 |  |  |  |
| MAX |  |  |  | 30 | 65 | 29 | 66 | 30 | 65 | 30 | 65 | 28 | 64 | 29 | 65 | 30 | 66 | 28 | 65 |  |  |  |

## PACKAGING MATERIAL STORE: AUGUST 2025

| S/N | DATE | TIME | DEPT | READINGS |  |  |  |  |  |  |  |  |  | MEAN |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  |  |  |
|  |  |  |  | T | H | T | H | T | H | T | H | T | H | T | H |
| 1 | 11/08/2025 | 9:00 AM | PMS | 23 | 62 | 21 | 65 | 24 | 61 | 22 | 64 | 23 | 62 | 22.6 | 62.8 |
|  |  | 11:00 AM | PMS | 24 | 61 | 25 | 59 | 23 | 62 | 26 | 60 | 24 | 58 | 24.4 | 60 |
|  |  | 1:00 PM | PMS | 28 | 56 | 27 | 58 | 26 | 57 | 25 | 59 | 27 | 56 | 26.6 | 57.2 |
|  |  | 3:00 PM | PMS | 30 | 54 | 29 | 55 | 28 | 53 | 27 | 56 | 29 | 54 | 28.6 | 54.4 |
| 2 | 12/08/2025 | 9:00 AM | PMS | 23 | 64 | 22 | 63 | 24 | 65 | 21 | 62 | 23 | 63 | 22.6 | 63.4 |
|  |  | 11:00 AM | PMS | 27 | 60 | 24 | 62 | 25 | 61 | 26 | 59 | 24 | 60 | 25.2 | 60.4 |
|  |  | 1:00 PM | PMS | 28 | 58 | 26 | 57 | 27 | 59 | 25 | 58 | 26 | 56 | 26.4 | 57.6 |
|  |  | 3:00 PM | PMS | 29 | 55 | 30 | 54 | 28 | 56 | 27 | 54 | 28 | 53 | 28.4 | 54.4 |
| 3 | 13/08/2025 | 9:00 AM | PMS | 22 | 63 | 23 | 64 | 21 | 62 | 24 | 65 | 22 | 63 | 22.4 | 63.4 |
|  |  | 11:00 AM | PMS | 26 | 60 | 25 | 61 | 24 | 63 | 23 | 59 | 24 | 62 | 24.4 | 61 |
|  |  | 1:00 PM | PMS | 27 | 57 | 28 | 56 | 26 | 58 | 27 | 59 | 25 | 57 | 26.6 | 57.4 |
|  |  | 3:00 PM | PMS | 30 | 54 | 28 | 55 | 29 | 54 | 27 | 56 | 28 | 55 | 28.4 | 54.8 |
| 4 | 14/08/2025 | 9:00 AM | PMS | 24 | 64 | 22 | 63 | 23 | 65 | 21 | 62 | 24 | 63 | 22.8 | 63.4 |
|  |  | 11:00 AM | PMS | 25 | 61 | 26 | 60 | 24 | 62 | 23 | 59 | 25 | 60 | 24.6 | 60.4 |
|  |  | 1:00 PM | PMS | 28 | 57 | 27 | 58 | 26 | 56 | 25 | 59 | 27 | 57 | 26.6 | 57.4 |
|  |  | 3:00 PM | PMS | 30 | 55 | 29 | 54 | 28 | 56 | 27 | 53 | 28 | 55 | 28.4 | 54.6 |
| 5 | 15/08/2025 | 9:00 AM | PMS | 23 | 63 | 24 | 62 | 22 | 64 | 23 | 65 | 21 | 63 | 22.6 | 63.4 |
|  |  | 11:00 AM | PMS | 26 | 60 | 24 | 61 | 25 | 62 | 23 | 59 | 24 | 60 | 24.4 | 60.4 |
|  |  | 1:00 PM | PMS | 27 | 58 | 28 | 57 | 26 | 59 | 25 | 56 | 27 | 58 | 26.6 | 57.6 |
|  |  | 3:00 PM | PMS | 29 | 54 | 27 | 55 | 28 | 53 | 30 | 56 | 28 | 54 | 28.4 | 54.4 |
| 6 | 16/08/2023 | 9:00 AM | PMS | 22 | 62 | 23 | 63 | 21 | 64 | 24 | 65 | 22 | 63 | 22.4 | 63.4 |
|  |  | 11:00 AM | PMS | 24 | 60 | 26 | 61 | 25 | 62 | 23 | 59 | 24 | 60 | 24.4 | 60.4 |
|  |  | 1:00 PM | PMS | 27 | 57 | 26 | 58 | 28 | 56 | 25 | 59 | 27 | 58 | 26.6 | 57.6 |
|  |  | 3:00 PM | PMS | 29 | 55 | 28 | 54 | 27 | 56 | 30 | 53 | 28 | 55 | 28.4 | 54.6 |
| 7 | 17/08/2023 | 9:00 AM | PMS | 23 | 63 | 22 | 64 | 24 | 62 | 21 | 65 | 23 | 63 | 22.6 | 63.4 |
|  |  | 11:00 AM | PMS | 25 | 61 | 24 | 60 | 26 | 62 | 23 | 59 | 24 | 60 | 24.4 | 60.4 |
|  |  | 1:00 PM | PMS | 27 | 58 | 26 | 57 | 28 | 56 | 25 | 59 | 27 | 58 | 26.6 | 57.6 |
|  |  | 3:00 PM | PMS | 30 | 54 | 29 | 55 | 28 | 53 | 27 | 56 | 28 | 54 | 28.4 | 54.4 |
| Mean |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.52857143 | 58.93571429 |
| MIN |  |  |  | 22 | 54 | 21 | 54 | 21 | 53 | 21 | 53 | 21 | 53 |  |  |
| MAX |  |  |  | 30 | 64 | 30 | 65 | 29 | 65 | 30 | 65 | 29 | 63 |  |  |

## APPROVED RAW MATERIAL STORE: AUGUST 2025

| S/N | DATE | TIME | DEPT | READINGS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | MEAN |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  |  |  |
|  |  |  |  | T | H | T | H | T | H | T | H | T | H | T | H | T | H | T | H | T | H |
| 1 | 11/08/2025 | 9:00 AM | ARM | 23 | 62 | 22 | 64 | 24 | 61 | 23 | 63 | 22 | 62 | 24 | 61 | 23 | 62 | 22 | 63 | 22.875 | 62.25 |
|  |  | 11:00 AM | ARM | 25 | 60 | 23 | 61 | 24 | 59 | 26 | 60 | 24 | 58 | 25 | 59 | 26 | 58 | 24 | 60 | 24.625 | 59.375 |
|  |  | 1:00 PM | ARM | 28 | 57 | 26 | 58 | 27 | 56 | 26 | 57 | 25 | 59 | 27 | 56 | 28 | 55 | 26 | 57 | 26.625 | 56.875 |
|  |  | 3:00 PM | ARM | 29 | 54 | 28 | 55 | 30 | 53 | 27 | 54 | 28 | 55 | 29 | 53 | 28 | 54 | 27 | 55 | 28.25 | 54.125 |
| 2 | 12/08/2025 | 9:00 AM | ARM | 22 | 63 | 21 | 65 | 23 | 62 | 22 | 64 | 24 | 63 | 23 | 62 | 22 | 63 | 23 | 62 | 22.5 | 63 |
|  |  | 11:00 AM | ARM | 24 | 61 | 26 | 60 | 25 | 59 | 23 | 61 | 24 | 60 | 25 | 59 | 26 | 58 | 24 | 60 | 24.625 | 59.75 |
|  |  | 1:00 PM | ARM | 27 | 58 | 26 | 57 | 28 | 59 | 25 | 56 | 27 | 57 | 26 | 56 | 27 | 55 | 26 | 57 | 26.5 | 56.875 |
|  |  | 3:00 PM | ARM | 28 | 54 | 29 | 55 | 27 | 53 | 28 | 54 | 26 | 55 | 27 | 54 | 28 | 53 | 27 | 54 | 27.5 | 54 |
| 3 | 13/08/2025 | 9:00 AM | ARM | 23 | 63 | 24 | 62 | 22 | 64 | 21 | 65 | 23 | 63 | 22 | 63 | 23 | 62 | 22 | 64 | 22.5 | 63.25 |
|  |  | 11:00 AM | ARM | 26 | 60 | 25 | 62 | 24 | 61 | 23 | 59 | 24 | 60 | 25 | 61 | 24 | 60 | 25 | 59 | 24.5 | 60.25 |
|  |  | 1:00 PM | ARM | 27 | 57 | 28 | 58 | 26 | 56 | 27 | 59 | 25 | 57 | 26 | 58 | 27 | 57 | 26 | 56 | 26.5 | 57.25 |
|  |  | 3:00 PM | ARM | 30 | 54 | 29 | 55 | 28 | 53 | 27 | 54 | 29 | 56 | 28 | 55 | 29 | 54 | 28 | 55 | 28.5 | 54.5 |
| 4 | 14/08/2025 | 9:00 AM | ARM | 21 | 64 | 23 | 63 | 22 | 65 | 24 | 62 | 22 | 63 | 23 | 62 | 22 | 64 | 23 | 63 | 22.5 | 63.25 |
|  |  | 11:00 AM | ARM | 24 | 60 | 25 | 61 | 26 | 59 | 23 | 60 | 24 | 61 | 25 | 60 | 24 | 61 | 25 | 60 | 24.5 | 60.25 |
|  |  | 1:00 PM | ARM | 28 | 56 | 27 | 57 | 26 | 58 | 25 | 59 | 27 | 57 | 26 | 58 | 27 | 57 | 26 | 58 | 26.5 | 57.5 |
|  |  | 3:00 PM | ARM | 29 | 55 | 28 | 54 | 30 | 56 | 27 | 53 | 28 | 55 | 29 | 54 | 28 | 55 | 27 | 54 | 28.25 | 54.5 |
| 5 | 15/08/2025 | 9:00 AM | ARM | 23 | 62 | 22 | 64 | 21 | 63 | 24 | 65 | 22 | 63 | 23 | 63 | 22 | 64 | 23 | 63 | 22.5 | 63.375 |
|  |  | 11:00 AM | ARM | 25 | 60 | 24 | 61 | 26 | 59 | 23 | 60 | 24 | 62 | 25 | 60 | 24 | 61 | 25 | 60 | 24.5 | 60.375 |
|  |  | 1:00 PM | ARM | 27 | 58 | 26 | 57 | 28 | 56 | 25 | 59 | 27 | 57 | 26 | 58 | 27 | 57 | 26 | 58 | 26.5 | 57.5 |
|  |  | 3:00 PM | ARM | 28 | 54 | 29 | 55 | 27 | 53 | 30 | 56 | 28 | 54 | 29 | 55 | 28 | 54 | 27 | 55 | 28.25 | 54.5 |
| 6 | 16/08/2023 | 9:00 AM | ARM | 22 | 63 | 23 | 62 | 24 | 64 | 21 | 65 | 22 | 63 | 23 | 62 | 22 | 64 | 23 | 63 | 22.5 | 63.25 |
|  |  | 11:00 AM | ARM | 26 | 60 | 24 | 61 | 25 | 59 | 23 | 62 | 24 | 60 | 25 | 60 | 24 | 61 | 25 | 60 | 24.5 | 60.375 |
|  |  | 1:00 PM | ARM | 27 | 57 | 28 | 58 | 26 | 59 | 27 | 56 | 25 | 57 | 26 | 58 | 27 | 57 | 26 | 58 | 26.5 | 57.5 |
|  |  | 3:00 PM | ARM | 29 | 55 | 28 | 54 | 27 | 56 | 30 | 53 | 28 | 55 | 29 | 54 | 28 | 55 | 27 | 54 | 28.25 | 54.5 |
| 7 | 17/08/2023 | 9:00 AM | ARM | 23 | 63 | 22 | 65 | 21 | 64 | 24 | 62 | 23 | 63 | 22 | 63 | 23 | 62 | 22 | 64 | 22.5 | 63.25 |
|  |  | 11:00 AM | ARM | 24 | 61 | 25 | 60 | 23 | 62 | 26 | 61 | 24 | 60 | 25 | 61 | 24 | 60 | 25 | 61 | 24.5 | 60.75 |
|  |  | 1:00 PM | ARM | 28 | 57 | 26 | 58 | 27 | 59 | 25 | 56 | 27 | 57 | 26 | 58 | 27 | 57 | 26 | 58 | 26.5 | 57.5 |
|  |  | 3:00 PM | ARM | 30 | 54 | 28 | 55 | 29 | 53 | 27 | 56 | 28 | 54 | 29 | 55 | 28 | 54 | 27 | 55 | 28.25 | 54.5 |
| Mean |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.44642857 | 58.72767857 |
| MIN |  |  |  | 21 | 54 | 21 | 54 | 21 | 53 | 21 | 53 | 22 | 54 | 22 | 53 | 22 | 53 | 22 | 54 |  |  |
| MAX |  |  |  | 30 | 64 | 29 | 65 | 30 | 65 | 30 | 65 | 29 | 63 | 29 | 63 | 29 | 64 | 28 | 64 |  |  |

## QUARANTINED RAW MATERIAL STORE: AUGUST 2025

| S/N | DATE | TIME | DEPT | READINGS |  |  |  |  |  |  |  |  |  | MEAN |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  |  |  |
|  |  |  |  | T | H | T | H | T | H | T | H | T | H | T | H |
| 1 | 11/08/2025 | 9:00 AM | QRMS | 23 | 62 | 22 | 64 | 21 | 63 | 23 | 62 | 22 | 63 | 22.2 | 62.8 |
|  |  | 11:00 AM | QRMS | 25 | 60 | 24 | 61 | 23 | 60 | 24 | 62 | 23 | 61 | 23.8 | 60.8 |
|  |  | 1:00 PM | QRMS | 26 | 57 | 25 | 58 | 27 | 59 | 26 | 57 | 25 | 58 | 25.8 | 57.8 |
|  |  | 3:00 PM | QRMS | 28 | 54 | 27 | 55 | 26 | 56 | 27 | 54 | 28 | 53 | 27.2 | 54.4 |
| 2 | 12/08/2025 | 9:00 AM | QRMS | 22 | 63 | 23 | 62 | 22 | 64 | 21 | 63 | 23 | 64 | 22.2 | 63.2 |
|  |  | 11:00 AM | QRMS | 24 | 61 | 25 | 60 | 24 | 62 | 23 | 61 | 25 | 60 | 24.2 | 60.8 |
|  |  | 1:00 PM | QRMS | 27 | 58 | 26 | 57 | 28 | 58 | 26 | 59 | 27 | 57 | 26.8 | 57.8 |
|  |  | 3:00 PM | QRMS | 29 | 55 | 28 | 54 | 27 | 56 | 28 | 55 | 29 | 54 | 28.2 | 54.8 |
| 3 | 13/08/2025 | 9:00 AM | QRMS | 21 | 63 | 22 | 62 | 23 | 64 | 22 | 63 | 21 | 64 | 21.8 | 63.2 |
|  |  | 11:00 AM | QRMS | 24 | 61 | 25 | 60 | 23 | 62 | 24 | 59 | 24 | 61 | 24 | 60.6 |
|  |  | 1:00 PM | QRMS | 26 | 58 | 27 | 57 | 26 | 59 | 27 | 56 | 26 | 57 | 26.4 | 57.4 |
|  |  | 3:00 PM | QRMS | 28 | 55 | 27 | 56 | 29 | 54 | 28 | 53 | 27 | 55 | 27.8 | 54.6 |
| 4 | 14/08/2025 | 9:00 AM | QRMS | 23 | 62 | 22 | 63 | 24 | 62 | 23 | 64 | 22 | 63 | 22.8 | 62.8 |
|  |  | 11:00 AM | QRMS | 25 | 61 | 24 | 60 | 26 | 60 | 24 | 61 | 25 | 59 | 24.8 | 60.2 |
|  |  | 1:00 PM | QRMS | 27 | 58 | 26 | 57 | 25 | 59 | 27 | 58 | 26 | 57 | 26.2 | 57.8 |
|  |  | 3:00 PM | QRMS | 29 | 56 | 27 | 54 | 28 | 55 | 27 | 56 | 28 | 54 | 27.8 | 55 |
| 5 | 15/08/2025 | 9:00 AM | QRMS | 22 | 63 | 21 | 64 | 23 | 63 | 22 | 62 | 23 | 64 | 22.2 | 63.2 |
|  |  | 11:00 AM | QRMS | 24 | 60 | 25 | 61 | 24 | 62 | 23 | 60 | 24 | 61 | 24 | 60.8 |
|  |  | 1:00 PM | QRMS | 27 | 58 | 26 | 57 | 25 | 59 | 27 | 58 | 26 | 57 | 26.2 | 57.8 |
|  |  | 3:00 PM | QRMS | 28 | 55 | 29 | 54 | 27 | 56 | 28 | 55 | 27 | 54 | 27.8 | 54.8 |
| 6 | 16/08/2023 | 9:00 AM | QRMS | 23 | 62 | 22 | 64 | 21 | 63 | 23 | 62 | 22 | 63 | 22.2 | 62.8 |
|  |  | 11:00 AM | QRMS | 25 | 60 | 24 | 61 | 23 | 60 | 25 | 61 | 24 | 59 | 24.2 | 60.2 |
|  |  | 1:00 PM | QRMS | 27 | 56 | 26 | 58 | 27 | 59 | 26 | 58 | 27 | 57 | 26.6 | 57.6 |
|  |  | 3:00 PM | QRMS | 28 | 53 | 27 | 56 | 29 | 54 | 27 | 55 | 28 | 54 | 27.8 | 54.4 |
| 7 | 17/08/2023 | 9:00 AM | QRMS | 22 | 62 | 23 | 63 | 22 | 64 | 21 | 63 | 23 | 62 | 22.2 | 62.8 |
|  |  | 11:00 AM | QRMS | 25 | 59 | 24 | 61 | 25 | 60 | 23 | 61 | 24 | 60 | 24.2 | 60.2 |
|  |  | 1:00 PM | QRMS | 27 | 57 | 26 | 58 | 25 | 57 | 26 | 58 | 27 | 56 | 26.2 | 57.2 |
|  |  | 3:00 PM | QRMS | 29 | 54 | 28 | 55 | 27 | 54 | 28 | 53 | 27 | 54 | 27.8 | 54 |
| Mean |  |  |  |  |  |  |  |  |  |  |  |  |  | 25.12142857 | 58.92142857 |
| MIN |  |  |  | 21 | 53 | 21 | 54 | 21 | 54 | 21 | 53 | 21 | 53 |  |  |
| MAX |  |  |  | 29 | 63 | 29 | 64 | 29 | 64 | 28 | 64 | 29 | 64 |  |  |

# SUMMARY OF DATA

| S/N | Unit | Average daily condition for the duration |  | Minimum for the duration |  | Maximum for the duration |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | T | H | T | H | T | H |
| 1 | A. Finished Goods Store | 25.403 | 59.101 | 21 | 53 | 29 | 66 |
| 2 | Q. Finished Goods Store | 25.3321 | 59.509 | 21 | 53 | 30 | 65 |
| 3 | Packaging Material Store | 25.529 | 59.936 | 21 | 53 | 30 | 65 |
| 4 | A. Raw Material Store | 25.446 | 58.728 | 21 | 53 | 30 | 65 |
| 5 | Q. Raw Material Store | 25.121 | 58.92 | 21 | 53 | 29 | 64 |

# DISCUSSION OF DATA

Environmental monitoring of temperature and relative humidity was conducted in the Finished Goods Stores, Raw Material Stores, and Packaging Material Store over the monitoring period. The results indicate that the average daily temperature across the monitored locations ranged from 25.121 °C to 25.529 °C, while the average relative humidity ranged from 58.728 % to 59.936 % RH. During the monitoring period, the recorded minimum temperature and relative humidity were 21 °C and 53 % RH, respectively, while the maximum temperature and relative humidity observed were 30 °C and 66 % RH.

Overall, the environmental conditions across all storage areas remained generally consistent and within acceptable operational ranges for controlled warehouse storage conditions, with only minor fluctuations observed during the monitoring period. The recorded values demonstrate that the facility maintains stable environmental control across the Finished Goods Store, Raw Material Store, and Packaging Material Store, indicating that the environmental control systems are functioning adequately to support proper storage conditions. Based on the results obtained, the monitored storage areas are considered suitable for the intended storage of materials and finished products under the specified environmental conditions.

# CONCLUSION

These results indicate that the environmental conditions within the monitored storage areas were adequately controlled and maintained within acceptable operational ranges for warehouse storage conditions. Overall, the monitoring data collected in August 2025 demonstrate that the facility’s environmental control systems are functioning effectively and that the storage areas are suitable for maintaining the quality and integrity of stored raw materials, packaging materials, and finished products.

# RECOMMENDATION

Environmental monitoring of temperature and relative humidity in all storage areas should be continued at the established frequency to ensure that the environmental conditions remain within acceptable limits for the storage of raw materials, packaging materials, and finished products. Continuous monitoring and proper documentation will help maintain compliance with good storage and Good Manufacturing Practice (GMP) requirements while ensuring that any variations in environmental conditions are promptly detected and addressed.

Preventive maintenance of the AHUs should be carried out regularly to ensure consistent environmental control within the facility. In addition, all temperature and humidity monitoring devices should be calibrated according to the approved calibration schedule to ensure the accuracy and reliability of recorded data used for quality and regulatory purposes.

The Quality Unit should perform periodic reviews of environmental monitoring records to identify any unusual trends, fluctuations, or deviations from the expected conditions. Any out-of-specification readings should be documented and investigated appropriately, and corrective and preventive actions should be implemented where necessary to prevent recurrence.

Furthermore, it is recommended that environmental monitoring be conducted again during the next season to assess potential seasonal variations in temperature and relative humidity within the storage areas. This will help confirm that the facility’s environmental control systems remain effective under different climatic conditions and will provide additional assurance of the suitability of the storage environment throughout the year.

# ATTACHMENT

The following attachments are provided for this report.

| s/no | Attachment | Description |
| --- | --- | --- |
| 1 | Graph | Graphical representation for temperature distribution for each store |
| 2 | Graph | Graphical representation for humidity distribution for each store |
| 3 | Graph | Graphical representation for periodic mean distribution for each store |

| FIGURES |  |  |
| --- | --- | --- |
| s/no | Figure | location |
| 1 | Fig. 1 | Approved Finished Goods Store |
| 2 | Fig. 2 | Quarantine Finished Goods Store |
| 3 | Fig. 3 | Packaging Material Store |
| 4 | Fig. 4 | Approved Raw Material Store |
| 5 | Fig. 6 | Quarantine Raw Material Store |

Fig. 1: distribution for the Approved Finished Goods Store

Fig. 2: distribution for the Quarantine Finished Goods Store

Fig. 3: distribution for the Packaging Material Store

Fig. 4: distribution for the Approved Raw Material Store

Fig. 5: environmental distribution for Quarantine Raw Material Store