BIOMEDICAL LIMITED

# WATER SYSTEM VALIDATION PROTOCOL

# (WFI Production System – GMP Critical)

LOCATION – WATER TREATMENT PLANT

PROTOCOL No. – BML/QA/WSP/001

PROVIDED BY:

BIOMEDICAL LIMTED

KWARA STATE, NIGERIA

Contents

APPROVAL PAGE	4

1. PURPOSE AND SCOPE	5

1.1 Purpose	5

1.2 Scope	5

2. REGULATORY REFERENCES AND STANDARDS	6

3. SYSTEM DESCRIPTION	7

3.1 Water Treatment Train Overview	7

3.1.1 Stage 1 — Borehole Abstraction & Raw Water Storage	7

3.1.2 Stage 2 — Multimedia Sand Filtration	7

3.1.3 Stage 3 — Activated Carbon Filtration	7

3.1.4 Stage 4 — Water Softening	7

3.1.5 Stage 5 — Demineralised Water Production (Ion Exchange)	8

3.1.6 Stage 6 — Reverse Osmosis (RO)	8

3.1.7 Stage 7 — Multicolumn Distillation Plant (MCDP)	8

3.1.8 Stage 8 — WFI Storage and Distribution	8

4. VALIDATION STRATEGY	9

4.1 Validation Life Cycle Approach	9

4.2 Qualification Activities	9

5. CRITICAL QUALITY ATTRIBUTES (CQAs) AND ACCEPTANCE CRITERIA	11

5.1 WFI — Pharmacopoeial Specification	11

5.2 Intermediate Water Quality Targets	11

6. CRITICAL PROCESS PARAMETERS (CPPs) AND MONITORING	13

6.1 MCDP Critical Process Parameters	13

6.2 RO Critical Process Parameters	13

6.3 Storage Tank and Loop Critical Parameters	14

7. SAMPLING PLAN	15

7.1 Phase 1 Sampling Plan (Weeks 1–2)	15

7.2 Phase 2 Sampling Plan (Weeks 3–4)	16

7.3 Phase 3 / Routine Monitoring Sampling Plan	17

8. TEST METHODS AND ANALYTICAL PROCEDURES	19

8.1 Physicochemical Tests	19

8.2 Microbiological Tests	20

8.3 Instrument Calibration and System Suitability	20

9. ALERT AND ACTION LIMITS — PROCEDURES	21

9.1 Definitions	21

9.2 Alert and Action Limit Table — WFI	21

9.3 Alert Exceedance Response Procedure	22

9.4 Action Limit Exceedance Response Procedure	22

10. SANITISATION AND MAINTENANCE REQUIREMENTS	23

10.1 WFI Storage and Distribution — Hot Water Sanitisation	23

10.2 Planned Maintenance Impact on Validation	24

11. DEVIATION MANAGEMENT, OOS RESULTS, AND CAPA	25

11.1 Out-of-Specification (OOS) Result Handling	25

11.2 Validation Failure Criteria	25

12. DOCUMENTATION AND DATA MANAGEMENT	26

12.1 Required Validation Documents	26

12.2 Data Integrity Requirements	27

13. CHANGE CONTROL AND RE-QUALIFICATION	28

13.1 Changes Requiring Re-qualification	28

14. ROLES AND RESPONSIBILITIES	29

15. GLOSSARY OF ABBREVIATIONS	31

16. APPENDICES	33

Appendix A — Sampling Location Map / P&ID Reference	33

Appendix B — Sampling Record Template	33

Appendix C — WFI System Sanitisation Log Template	34

Appendix D — Phase Summary Acceptance Checklist	34

PROTOCOL FORMAT APPROVAL:

Signatures on this page indicate that this document and its format have been prepared, checked and approved by the personnel concerned. It shall be signed and date as shown below

|  | PREPARED BY: | REVIEWED BY: |
| --- | --- | --- |
| Signature: |  |  |
| Position: |  |  |
| Date: |  |  |

|  | APPROVED BY: | AUTHORIZED BY: |
| --- | --- | --- |
| Signature: |  |  |
| Position: |  |  |
| Date: |  |  |

# 1. PURPOSE AND SCOPE

## 1.1 Purpose

This Validation Protocol defines the strategy, methodology, acceptance criteria, and documentation requirements for the validation of the Water for Injection (WFI) production system. The validation demonstrates that the complete water system consistently produces WFI meeting the requirements of the European Pharmacopoeia (Ph. Eur.), British Pharmacopeia (BP), and applicable GMP regulations.

## 1.2 Scope

This protocol covers the entire water purification train from source water to WFI point-of-use, encompassing the following treatment stages:

- Borehole abstraction and raw water storage tanks

- Multimedia sand filtration

- Activated carbon filtration

- Water softening (ion exchange — cation resin, sodium regeneration)

- Ion exchange demineralisation (two-bed deionisation)

- Reverse Osmosis (RO) — double pass

- Multicolumn Distillation Plants (MCDP) for WFI generation

- WFI storage tanks (jacketed, with CIP capability)

- WFI distribution loop — all points of use

The following are excluded from this protocol:

- Process water (purified water) distribution loops not associated with the WFI system

- Steam generation systems validated under a separate steam qualification protocol

- Cleaning validation of downstream manufacturing equipment.

# 2. REGULATORY REFERENCES AND STANDARDS

| Reference | Description |
| --- | --- |
| Ph. Eur. 0169 | Water for Injections — specification and production requirements |
| USP <1231> | Water for Pharmaceutical Purposes |
| EU GMP Annex 1 (2022) | Manufacture of Sterile Medicinal Products |
| EU GMP Chapter 3 | Premises and Equipment |
| EU GMP Chapter 4 | Documentation |
| ICH Q9 | Quality Risk Management |
| ISPE Baseline Guide Vol. 4 | Water and Steam Systems |

# 3. SYSTEM DESCRIPTION

## 3.1 Water Treatment Train Overview

The WFI production system is a multi-stage purification train designed to progressively reduce chemical, microbiological, and particulate contamination from borehole source water to pharmacopoeial WFI standard. The complete process train is described below:

### 3.1.1 Stage 1 — Borehole Abstraction & Raw Water Storage

Source water is abstracted from 2 boreholes equipped with submersible pumps. Raw water is transferred to buffer storage tanks (capacity: 10000 L) prior to treatment. Storage tanks are sealed with vent filters. Overflow and drain connections are indirect to prevent back-contamination.

### 3.1.2 Stage 2 — Multimedia Sand Filtration

Raw water passes through multimedia sand filter vessels containing graded layers of anthracite, sand, and gravel. This stage removes suspended solids, turbidity, and coarse particulates. Filters are backwashed automatically based on differential pressure and timed cycles. Backwash water is directed to drain.

### 3.1.3 Stage 3 — Activated Carbon Filtration

Granular activated carbon (GAC) filter vessels remove chlorine, chloramines, organic compounds, taste, and odour. Carbon beds are periodically sanitised by hydrogen peroxide solution to control microbial growth. The filter is also periodically backwashed to removed adsorbed matter. Bed replacement is based on performance monitoring and scheduled change-out intervals.

### 3.1.4 Stage 4 — Water Softening

Cation exchange resin vessels (sodium form) remove hardness ions (Ca²⁺, Mg²⁺) by exchange with sodium ions. Softeners are regenerated with pharmaceutical-grade sodium chloride solution on a timed-triggered basis. Hardness breakthrough is monitored and triggers manual regeneration.

### 3.1.5 Stage 5 — Demineralised Water Production (Ion Exchange)

Demineralised water (DM water) is produced via two-bed ion exchange systems. Cation resin (H⁺ form) removes cations; anion resin (OH⁻ form) removes anions. Conductivity and pH are continuously monitored. Exhausted resin beds are regenerated with acid (HCl) and caustic (NaOH). DM water is used as feed to the RO system.

### 3.1.6 Stage 6 — Reverse Osmosis (RO)

The RO system (double pass) uses semipermeable membranes operating at elevated pressure (typically 8–15 bar) to remove dissolved ions, organics, endotoxins, and microorganisms. Permeate conductivity, pressure, flow, and recovery rate are continuously monitored. Reject is directed to drain. Membranes are sanitised by peroxide water recirculation (periodic). RO permeate serves as feed water for the MCDP.

### 3.1.7 Stage 7 — Multicolumn Distillation Plant (MCDP)

The MCDP is the primary WFI generation unit. It operates on the principle of multiple-effect distillation, where feed water is evaporated and condensed across 4 columns (effects), each at progressively lower pressure and temperature. The first effect is heated by clean steam at 4 bar. Each subsequent effect is heated by the vapour generated in the preceding column. The WFI distillate is collected in a vapour separator to ensure separation from entrained water droplets and any residual pyrogens.

The MCDP operates continuously at temperatures ensuring bactericidal conditions (≥80°C for storage; distillation temperatures >121°C in early effects). This self-sanitising operation is fundamental to the hygienic design of the WFI system.

### 3.1.8 Stage 8 — WFI Storage and Distribution

Freshly distilled WFI is collected in jacketed storage tanks (capacity: 4000 L) maintained at ≥80°C (hot storage) to prevent microbial growth. Tanks are equipped with hydrophobic vent filters (0.22 μm), spray ball for CIP, level indication, temperature probes, and pressure relief. WFI is distributed continuously via a circulating loop (heated to ≥80°C) to all points of use (POU). All pipework is 316L stainless steel, electropolished internally, with orbital-welded connections.

# 4. VALIDATION STRATEGY

## 4.1 Validation Life Cycle Approach

Validation follows the WHO -recommended three-phase approach for water systems, integrated within the overall validation life cycle:

| Phase | Period | Description |
| --- | --- | --- |
| Phase 1 | 2 weeks | Intensive monitoring during commissioning. All parameters, all sampling points, every day. Demonstrates initial compliance and identifies system characteristics. |
| Phase 2 | 2 weeks | Extended monitoring under normal operational conditions including seasonal variation. Sampling frequency remains high. Demonstrates consistent performance under routine operation. |
| Phase 3 | 12 months | Routine monitoring under full operational conditions across all seasons. Demonstrates long-term consistency and establishes alert/action limits. Transitions to ongoing monitoring program. Reduced testing frequency. |

## 4.2 Qualification Activities

The following formal qualification documents are required and must be approved prior to the commencement of validation activities:

| Activity | Document Ref. | Scope |
| --- | --- | --- |
| URS |  | User requirements for the complete water system |
| Risk Assessment |  | FMEA / risk assessment for water system components |
| DQ |  | Design Qualification of MCDP, RO, storage, and distribution |
| IQ | BML/ENGR/XXXIQX/001 | Installation Qualification of all system components |
| OQ | BML/ENGR/XXXOQX/001 | Operational Qualification — all instruments, alarms, controls |
| PQ Phase | BML/ENGR/XXXPQX/001 | Performance Qualification Phase — intensive sampling |

# 5. CRITICAL QUALITY ATTRIBUTES (CQAs) AND ACCEPTANCE CRITERIA

## 5.1 WFI — Pharmacopoeial Specification

WFI must comply with Ph. Eur. 0169 and USP <1231> at all times. The following are the critical quality attributes:

| Parameter | Ph. Eur. Limit | USP Limit | Alert Limit (Internal) |
| --- | --- | --- | --- |
| Conductivity (25°C) | ≤1.3 μS/cm | ≤1.3 μS/cm | ≤0.5 μS/cm |
| TOC (Total Organic Carbon) | ≤0.5 mg/L (500 ppb) | ≤0.5 mg/L | ≤0.25 mg/L |
| Endotoxins (LAL) | ≤0.25 EU/mL | ≤0.25 EU/mL | ≤0.125 EU/mL |
| Bioburden (plate count) | ≤10 CFU/100 mL | ≤10 CFU/100 mL | ≤5 CFU/100 mL |
| Nitrates | ≤0.2 ppm | ≤0.2 ppm | ≤0.1 ppm |
| Heavy Metals | ≤0.1 ppm | ≤0.1 ppm | ≤0.05 ppm |
| pH (informational) | 5.0–7.0 | 5.0–7.0 | 5.5–6.5 |
| Appearance | Clear, colourless | Clear, colourless | N/A |
| Particulates (≥10 μm) | Ph. Eur. 2.9.19 | USP <788> | Per Ph. Eur. 2.9.19 |

**internal alert limit shall reset to statistical validated history limits trending.

## 5.2 Intermediate Water Quality Targets

The following in-process quality targets apply at each treatment stage to ensure adequate performance of upstream units and protection of downstream processes:

| Stage / Point | Conductivity | Bioburden | Other Key Parameter |
| --- | --- | --- | --- |
| Borehole / Raw Water | Report | Report | Turbidity ≤1 NTU target |
| Post Sand Filter | Report | ≤500 CFU/mL | Turbidity ≤0.5 NTU |
| Post Carbon Filter | Report | ≤100 CFU/mL | Chlorine = ND |
| Post Softener | Report | ≤100 CFU/mL | Hardness ≤1 °dH |
| Post Ion Exchanger (DM) | ≤5.1 μS/cm | ≤50 CFU/mL | ROE, pH, TOC |
| Post RO Permeate | ≤1.3 μS/cm | ≤10 CFU/mL | ROE, pH, TOC |
| MCDP Feed Water | ≤1.3 μS/cm | ≤10 CFU/mL | Endotoxin ≤1 EU/mL, TOC, pH |
| WFI — MCDP Outlet | ≤1.3 μS/cm | ≤10 CFU/100 mL | Endotoxin ≤0.25 EU/mL, TOC, pH |
| WFI Storage Tank | ≤1.3 μS/cm | ≤10 CFU/100 mL | Temp ≥80°C maintained |
| WFI Loop — All POU | ≤1.3 μS/cm | ≤10 CFU/100 mL | Endotoxin ≤0.25 EU/mL |

# 6. CRITICAL PROCESS PARAMETERS (CPPs) AND MONITORING

## 6.1 MCDP Critical Process Parameters

| Parameter | Normal Range | Alarm Limit | Action |
| --- | --- | --- | --- |
| Column 1 temperature | ≥ 85 °C | < 85 °C | Stop production, investigate |
| Clean steam pressure (feed) | 4 bar(g) | < 4 bar(g) | Alarm, check steam supply |
| Feed water flow rate | 3000 L/hr | - | - |
| WFI conductivity (online) | ≤1.3 μS/cm | >1.3 μS/cm alert | Divert to drain, investigate |
| Distillate temperature | ≥ 85 °C | < 85 °C | Stop collection, divert to drain |
| Distillation rate / yield | 400–3000 L/hr | Drop >20% from baseline | Inspect columns, check fouling |

## 6.2 RO Critical Process Parameters

| Parameter | Normal Range | Alarm Limit | Action |
| --- | --- | --- | --- |
| Feed pressure | 100–150 bar | Outside range | Alarm, check pump/membranes |
| Permeate conductivity | ≤5 μS/cm | >5 μS/cm | Alarm, check membrane integrity |

## 6.3 Storage Tank and Loop Critical Parameters

| Parameter | Normal Range | Alarm Limit | Action |
| --- | --- | --- | --- |
| WFI tank temperature | ≥80°C | <75°C | Alarm, do not use, heat up, investigate |
| Loop circulation flow | Continuous ≥ 3000 L/hr | Stopped | Restart immediately, investigate |
| Loop return temperature | ≥80°C | <78°C | Alarm, increase heat trace/jacket |
| Tank level | 10%–90% | Outside range | Alarm, adjust production/use |

# 7. SAMPLING PLAN

## 7.1 Phase 1 Sampling Plan (Weeks 1–2)

During Phase 1, intensive daily sampling is required at all sampling points throughout the entire water treatment train and distribution loop. No sampling point may be omitted during Phase 1.

| Sampling Location | Frequency | Sample Volume | Tests Performed |
| --- | --- | --- | --- |
| PRE-TREATMENT |  |  |  |
| Raw Water (Borehole) | 3×/week | 1000 mL | Conductivity, pH, hardness, turbidity, coliforms |
| Post Sand Filter | Daily | 1000 mL | Turbidity, conductivity, bioburden |
| Post Carbon Filter | Daily | 1000 mL | Conductivity, chlorine, bioburden, TOC |
| Post Softener | Daily | 1000 mL | Hardness, conductivity, bioburden |
| DEMINERALISATION & RO |  |  |  |
| Post Ion Exchanger (DM Water) | Daily | 1000 mL | Conductivity, pH, ROE, bioburden, TOC, Nitrates, |
| RO Permeate | Daily | 1000 mL | Conductivity, TOC, bioburden, endotoxin, pH |
| RO Reject | Weekly | 1000 mL | Conductivity, TDS (for rejection calculation), TOC |
| WFI PRODUCTION — MCDP |  |  |  |
| MCDP Feed (RO product) | Daily | 1000 mL | Conductivity, bioburden, endotoxin |
| MCDP Outlet / WFI Collection | Daily × 2 (AM/PM) | 1000 mL | Full WFI spec: conductivity, TOC, endotoxin, bioburden, appearance, pH, nitrates, heavy metals |
| WFI STORAGE AND DISTRIBUTION |  |  |  |
| WFI Storage Tank — Inlet | Daily | 1000 mL | pH, Conductivity, TOC, endotoxin, bioburden |
| WFI Storage Tank — Outlet | Daily | 1000 mL | Full WFI spec |
| WFI Loop — Return (pre-tank) | Daily | 1000 mL | pH, Conductivity, TOC, endotoxin, bioburden |
| All POU Outlets (each) | Daily (rotate) | 1000 mL | Full WFI spec — rotate so each POU tested ≥2×/week |

## 7.2 Phase 2 Sampling Plan (Weeks 3–4)

Phase 2 sampling is reduced from Phase 1 but remains frequent. All WFI contact points must be sampled at least 3 times per week. Pre-treatment points may be sampled 3 times per week unless adverse trends are observed.

| Sampling Zone | Frequency | Notes |
| --- | --- | --- |
| Raw water / borehole | 2×/week | Continue monitoring for seasonal changes |
| Pre-treatment (sand, carbon, softener) | 2×/week | Monitor for microbial trends |
| Ion exchange DM water, RO permeate | 3×/week | Include endotoxin 1×/week |
| MCDP outlet — WFI quality | Daily | Full spec; retain samples per SOP |
| WFI storage tanks | Daily | Monitor both inlet and outlet |
| WFI loop return | Daily | Conductivity online + grab sample 3×/week |
| All Points of Use | Minimum 3×/week each | Rotate on schedule; document rotation |

## 7.3 Phase 3 / Routine Monitoring Sampling Plan

Phase 3 establishes the ongoing routine monitoring program. Routine monitoring continues indefinitely and data is reviewed at minimum monthly. Alert and action limits from Phases 1 and 2 are used to set statistical control limits.

| Sampling Zone | Minimum Frequency | Notes |
| --- | --- | --- |
| Borehole / raw water | 2x / week | Seasonal variation assessment; full chemical panel annually |
| Pre-treatment stages | 2×/week | Bioburden focus; conductivity |
| DM water / RO permeate | 2×/week | pH, Conductivity, TOC, bioburden; endotoxin monthly |
| WFI — MCDP outlet | Daily | pH, Conductivity, TOC online; bioburden |
| WFI storage tanks | Daily | Temperature continuous; bioburden |
| WFI loop return | Daily | Conductivity continuous; bioburden |
| Points of Use | Weekly each | Full spec per POU; bioburden |

# 8. TEST METHODS AND ANALYTICAL PROCEDURES

## 8.1 Physicochemical Tests

| Test | Method / Reference | Instrument | Frequency / Notes |
| --- | --- | --- | --- |
| Conductivity | Ph. Eur. 2.2.38 / USP <645> | Calibrated conductivity meter | Continuous online; daily grab |
| TOC | Ph. Eur. 2.2.44 / USP <643> | TOC analyser | Continuous or ≥daily; system suitability per Ph. Eur. |
| pH | Ph. Eur. 2.2.3 | Calibrated pH meter (2-point cal) | Per sampling schedule |
| Nitrates | Ph. Eur. 2.4.20 | UV spectrophotometry | Per sampling schedule |
| Heavy Metals | Ph. Eur. 2.4.8 | AAS (outsourced or in-house method) | Quarterly or as per schedule |
| Hardness | APHA 2340C (EDTA titrimetric) | Titration or photometer | Post-softener, per schedule |
| Turbidity | ISO 7027 / NTU | Turbidimeter | Pre-treatment, per schedule |
| Chlorine (total/free) | DPD colorimetric / photometry | Photometer or titration | Post carbon filter, per schedule |

## 8.2 Microbiological Tests

| Test | Method | Incubation / Reporting | Limit |
| --- | --- | --- | --- |
| Total Viable Count (TVC) | Membrane filtration (Ph. Eur. 2.6.12) on R2A or TGEA agar | 30–35°C, 72 hr (R2A: 25°C, 5 days) | WFI: ≤10 CFU/100 mL |
| Endotoxins (LAL) | Gel clot or kinetic turbidimetric (Ph. Eur. 2.6.14 / USP <85>) | As per validated method; BET | WFI: ≤0.25 EU/mL |
| Total Coliform (raw water) | Membrane filtration on LTB/MLSB | 35°C, 24–48 hr | Absent in 100 mL (raw water monitoring) |
| Microbial ID (OOS isolates) | MALDI-TOF or 16S rRNA sequencing | Per laboratory SOP | Identification of alert-triggering organisms |
| Environmental Monitoring | Settle plates, contact plates at POU areas | 30–35°C, 48–72 hr | As per area classification limits |

## 8.3 Instrument Calibration and System Suitability

- All instruments used for WFI testing are calibrated against traceable standards prior to each phase and at defined intervals (minimum annually)

- Online conductivity and TOC instruments undergo system suitability verification per Ph. Eur. 2.2.44 and 2.2.38 before and during each validation phase

- Endotoxin testing: BET validation (spike recovery, inhibition/enhancement testing) required per Ph. Eur. 2.6.14 for each water matrix tested

- All reference standards are within expiry date and traceable to a national metrology institute (e.g., NIST, NPL, EURAMET)

- Calibration records are maintained and available for regulatory inspection

# 9. ALERT AND ACTION LIMITS — PROCEDURES

## 9.1 Definitions

Alert Limit: A level that, when exceeded, triggers investigation and increased monitoring but does not automatically require rejection of water or cessation of production. The alert limit is set below the action limit and below the pharmacopoeial specification.

Action Limit: A level that, when exceeded, requires immediate corrective action including cessation of supply from the affected point, investigation, and formal CAPA. Water produced during an exceedance may be quarantined pending investigation.

## 9.2 Alert and Action Limit Table — WFI

| Parameter | Alert Limit | Action Limit | Specification Limit |
| --- | --- | --- | --- |
| Conductivity | ≤0.4 μS/cm | >0.5 μS/cm | ≤1.3 μS/cm |
| TOC | ≤0.2 mg/L | >0.25 mg/L | ≤0.5 mg/L |
| Endotoxins | ≤0.125 EU/mL | ≤0.25 EU/mL | ≤0.25 EU/mL |
| Bioburden | ≤4 CFU/100 mL | >7 CFU/100 mL | ≤10 CFU/100 mL |

## 9.3 Alert Exceedance Response Procedure

- Document the alert result in the QMS immediately

- Notify QA and Engineering within the hour

- Increase sampling frequency at the affected and adjacent points (double frequency for minimum 5 working days)

- Review trending data for the past 30 days — look for upward trends or previous marginal results

- Check CPP data (temperatures, pressures, flow rates) for the period surrounding the exceedance

- Review maintenance, regeneration, and sanitisation logs for the affected system stage

- Conduct root cause investigation — complete within 2 working days

- Complete an Investigation Report and close with documented conclusion

- Return to normal sampling frequency only after ≥5 consecutive compliant results at the affected point

## 9.4 Action Limit Exceedance Response Procedure

- Immediately quarantine any water produced from the affected storage tank or loop zone

- Cease supply to manufacturing processes — notify Production Manager and QA Responsible Person

- Isolate the affected section if possible without compromising the entire loop

- Open a formal deviation / non-conformance in the QMS

- Conduct emergency sampling at all upstream stages to identify the source

- Perform system flush and sanitisation per Sanitisation SOP

- Sample post-sanitisation (minimum 3 consecutive samples per affected point) — must meet specification before resuming supply

- Complete full CAPA including effectiveness check

- Brief senior management and consider regulatory notification if systemic failure is indicated

- Review and update risk assessment if root cause reveals new failure mode

# 10. SANITISATION AND MAINTENANCE REQUIREMENTS

## 10.1 WFI Storage and Distribution — Hot Water Sanitisation

The primary sanitisation mechanism for the WFI storage and distribution system is maintenance of ≥80°C at all times during hot operation. In addition, periodic thermal sanitisation cycles are performed at ≥121°C (where system design permits) or ≥80°C for extended periods per approved SOP.

| Component | Sanitisation Method | Frequency / Criteria |
| --- | --- | --- |
| WFI storage tanks | Hot water CIP (≥80°C) | Minimum weekly formal CIP; continuous hot operation |
| WFI distribution loop | Hot water circulation (≥80°C) | Continuous — temperature monitored at return |
| MCDP | Self-sanitising (operating temperature) | Continuous — operating temp ≥80°C; full drain/flush quarterly |
| RO membranes | chemical (H₂O2) | Weekly water flush; chemical per SOP if indicated by bioburden trend and then monthly chemical flush |
| Carbon filters | chemical sanitisation | Monthly minimum; or when bioburden trend increases |
| Ion exchange resin beds | chemical flush (H₂O2) | Following regeneration cycle; full sanitise Monthly chemical flush. |
| Sand filters | Backwash + chemical flush | formal wash monthly |
| Tank vent filters | Integrity test; replace | Test every 6 months; replace annually or on failure |
| Sampling valves / POU valves | Flaming before sampling | Each sampling event for microbiological testing, per sampling SOP |

## 10.2 Planned Maintenance Impact on Validation

All planned maintenance activities on the water system must be assessed for potential impact on validated state. The following rules apply:

- Any replacement of membrane, resin, or filter media requires post-change sampling before WFI production resumes — minimum 3 consecutive compliant samples at all downstream points

- Any break in the WFI loop (opening of sealed pipework, replacement of gaskets or valves) requires sanitisation and re-qualification sampling — minimum 5 consecutive compliant samples

- MCDP column inspections require full recommissioning and at minimum 2 days of intensive sampling before resumption of normal production

- Changes to CPP setpoints (temperatures, pressures) require formal change control and OQ re-testing

- All maintenance must be documented in the Maintenance Management System (MMS) and cross-referenced to the water system logbook

# 11. DEVIATION MANAGEMENT, OOS RESULTS, AND CAPA

## 11.1 Out-of-Specification (OOS) Result Handling

An OOS result is any analytical result that fails to meet the pharmacopoeial specification or the internal action limit for a defined parameter. The following procedure must be followed for all OOS results:

- Phase 1 — Laboratory Investigation: Review the original analytical data, instrument calibration records, standard preparation, and analyst technique for assignable cause. Complete within 1 working day.

- Phase 2 — Invalidation (if laboratory error confirmed): If a confirmed laboratory error is identified (instrument failure, transcription error, reagent OOS), the original result may be invalidated. Full documentation is required. Re-test the retained sample or original sample volume.

- Phase 3 — System Investigation (if no laboratory error): If no laboratory cause is found, commence full system investigation. Sample all upstream stages. Review CPP data. Engage Engineering and QA.

- Phase 4 — Corrective Action: Implement corrective action based on root cause (e.g., sanitise, replace component, adjust setpoint, increase regeneration frequency).

- Phase 5 — Verification Sampling: Following corrective action, collect a minimum of 3–5 consecutive compliant results from the affected point before returning to routine monitoring.

- Phase 6 — CAPA and Close-Out: Complete formal CAPA document. Assign effectiveness check with defined timeframe (minimum 30 days post-implementation). Close CAPA with QA approval.

## 11.2 Validation Failure Criteria

The validation is considered to have failed if any of the following occur during Phases 1 or 2:

- Any WFI result fails the pharmacopoeial specification (Ph. Eur. 0169 or USP <1231>) without a confirmed laboratory invalidation

- More than two alert limit exceedances at the same sampling point within any 10-day period

- Any confirmed endotoxin result >0.25 EU/mL in WFI

- Any confirmed bioburden result >10 CFU/100 mL in WFI

- Failure to maintain critical process parameter controls for a period exceeding [X] hours without immediate recovery

In the event of validation failure, Phase 1 must be repeated from the beginning after the root cause has been identified, corrective action implemented, and system re-qualified.

# 12. DOCUMENTATION AND DATA MANAGEMENT

## 12.1 Required Validation Documents

| Document | Owner | Requirement |
| --- | --- | --- |
| This Validation Protocol (VP) | QA | Approved before Phase 1 start |
| Validation Report — Phase 1 | QA | Completed within 10 WD of Phase 1 end |
| Validation Report — Phase 2 | QA | Completed within 10 WD of Phase 2 end |
| Validation Report — Phase 3 (Annual) | QA | Annual review and report |
| Sampling Schedules / SOPs | QC Laboratory | Approved before sampling begins |
| Analytical Methods / SOPs | QC Laboratory | Validated / verified before use |
| Instrument Calibration Records | QC Laboratory | Current at time of use |
| Water System Logbook | Engineering / Production | Real-time; all events, maintenance, deviations |
| CPP Continuous Data ( | Engineering | Archived; minimum 5 years retention |
| LIMS /Laboratory Data Records | QC | 21 CFR Part 11 / EU Annex 11 compliant |
| Deviation / OOS Records | QA | Linked to relevant sampling events |
| CAPA Records | QA | Closed with effectiveness verification |
| Change Control Records | QA / Engineering | All changes post-validation must be controlled |

## 12.2 Data Integrity Requirements

- All raw data (analytical results, instrument printouts, meta data) must be attributable, legible, contemporaneous, original, and accurate (ALCOA+ principles)

- Electronic data must comply with Annex 11 (EU) and/or 21 CFR Part 11 (FDA) as applicable

- Handwritten records must be signed, dated, and written in indelible ink; corrections made with single strikethrough, signed, and dated

- LIMS records if available are the master record; LIMS must be validated and access controlled

- Audit trails for all electronic systems must be enabled, reviewed regularly, and retained for a minimum of 5 years (or product lifetime + 1 year if longer)

- Sample chain of custody must be documented from collection to result entry

# 13. CHANGE CONTROL AND RE-QUALIFICATION

## 13.1 Changes Requiring Re-qualification

The following changes to the water system must be subject to formal change control and assessed for re-qualification impact before implementation:

| Change Type | Minimum Re-qualification | Notes |
| --- | --- | --- |
| Replacement of MCDP column(s) | OQ + PQ Phase 1 repeat | Full IQ if new equipment |
| RO membrane replacement (all or partial) | OQ re-test + 2 weeks intensive sampling | Salt rejection test required |
| New borehole or change in raw water source | PQ Phase 1 full repeat | Full chemical characterisation of new source |
| Addition of new POU point to loop | Sampling at new POU for 4 weeks before routine | Loop flow modelling review |
| Change in WFI storage temperature setpoint | OQ re-test; PQ Phase 2 repeat | Risk assessment required |
| Change in sanitisation agent/method | Method validation + PQ Phase 1 repeat | Microbial efficacy data required |
| Major pipework modification (loop) | IQ update + OQ + 4 weeks intensive sampling | P&ID update required |
| Carbon bed media replacement | OQ performance test + 2 weeks monitoring | Chlorine removal efficacy |
| Ion exchange resin replacement | OQ + conductivity verification + 2 weeks monitoring | New resin qualification data |
| Software / SCADA changes | Computer system validation (CSV) review | Annex 11 / GAMP5 compliant |

# 14. ROLES AND RESPONSIBILITIES

| Role | Responsibilities |
| --- | --- |
| Factory Manager/Supt Pharm | Protocol approval; final sign-off on validation reports; regulatory accountability; approval of deviations with quality impact |
| QA Manager | Review and approval of protocol and reports; deviation review and CAPA oversight; change control; data integrity governance; preparation of regulatory submissions |
| QC Chemist | Protocol authorship; coordination of validation activities; compilation of reports; facilitation of investigations; management of validation master plan entry |
| QC Head | Approval of sampling SOPs and analytical methods; oversight of sampling execution; LIMS management; OOS investigations; laboratory calibration programme |
| QC Analysts | Execution of sampling per approved SOPs; preparation and analysis of samples; recording of results in LIMS; flagging of OOS results to QC Manager |
| Engineering Manager | IQ/OQ execution and approval; maintenance programme management; CPP data provision; technical investigation support; change control technical review |
| Production Manager | Scheduling of validation activities; coordination with manufacturing; reporting of process deviations with water system impact; operator training oversight |
| Process Operator / Process Engineer | Daily operation of water system per SOPs; completion of water system logbook; reporting of abnormal conditions; execution of sanitisation procedures |

# 15. GLOSSARY OF ABBREVIATIONS

| Abbreviation | Definition |
| --- | --- |
| ALCOA+ | Attributable, Legible, Contemporaneous, Original, Accurate (+ Complete, Consistent, Enduring, Available) |
| BET | Bacterial Endotoxins Test |
| BMS | Building Management System |
| CAPA | Corrective and Preventive Action |
| CFR | Code of Federal Regulations |
| CFU | Colony Forming Units |
| CIP | Clean In Place |
| CPP | Critical Process Parameter |
| CQA | Critical Quality Attribute |
| CSV | Computer System Validation |
| DM Water | Demineralised Water |
| DQ | Design Qualification |
| EU | Endotoxin Units |
| EU GMP | European Union Good Manufacturing Practice |
| FMEA | Failure Mode and Effects Analysis |
| GAC | Granular Activated Carbon |
| GMP | Good Manufacturing Practice |
| IQ | Installation Qualification |
| ISPE | International Society for Pharmaceutical Engineering |
| LAL | Limulus Amebocyte Lysate |
| LIMS | Laboratory Information Management System |
| MCDP | Multicolumn Distillation Plant |
| MMS | Maintenance Management System |
| NTU | Nephelometric Turbidity Units |
| OQ | Operational Qualification |
| OOS | Out of Specification |
| P&ID | Piping and Instrumentation Diagram |
| Ph. Eur. | European Pharmacopoeia |
| POU | Point of Use |
| PQ | Performance Qualification |
| QA | Quality Assurance |
| QC | Quality Control |
| QMS | Quality Management System |
| QP | Qualified Person |
| rFC | Recombinant Factor C (endotoxin test) |
| RO | Reverse Osmosis |
| SCADA | Supervisory Control and Data Acquisition |
| SOP | Standard Operating Procedure |
| TOC | Total Organic Carbon |
| TVC | Total Viable Count |
| URS | User Requirements Specification |
| USP | United States Pharmacopeia |
| WFI | Water for Injections |

# 16. APPENDICES

## Appendix A — Sampling Location Map / P&ID Reference

The sampling locations defined in this protocol are identified on the approved P&ID drawing(s):

- Drawing No.: [P&ID-WS-001] — Water Treatment Train (Borehole to RO)

- Drawing No.: [P&ID-WS-002] — MCDP and WFI Storage/Distribution

- Sampling points are marked with tag numbers SP-WS-001 through SP-WS-[XX]

Note: A current, approved P&ID must be available in the validation report. Any P&ID revisions must be captured under change control.

## Appendix B — Sampling Record Template

| Sample ID | Date/Time | Location / POU | Sample Vol (mL) | Analyst | Tests Requested |
| --- | --- | --- | --- | --- | --- |

## Appendix C — WFI System Sanitisation Log Template

| Date | Component Sanitised | Method Used | Duration | Operator | QA Review |
| --- | --- | --- | --- | --- | --- |

## Appendix D — Phase Summary Acceptance Checklist

The following checklist must be completed and signed by QA prior to approval of each validation phase:

| Checklist Item | Yes / No | Initials |
| --- | --- | --- |
| All sampling events completed per approved schedule |  |  |
| No unresolved OOS results at close of phase |  |  |
| All deviations have been documented and closed (or justified open) |  |  |
| All CPP data has been reviewed and trends documented |  |  |
| All instrument calibrations were current during sampling period |  |  |
| Water system logbook is complete with no unexplained gaps |  |  |
| All acceptance criteria have been met for this phase |  |  |
| Phase validation report has been reviewed and is ready for approval |  |  |