| S.N | AUDIT FINDINGS (OBSERVATION) | ROOT CAUSE ANALYSIS | CORRECTIVE ACTION | INDICATORS FOR COMPLETION | TIMELINE | RESPONSIBILITY | CAPA STATUS |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CRITICAL |  | ENGINEERING |  |  |  |  |  |
| 1 | - WFI storage tank was observed to be washed manually with no evidence of disinfection after such process of washing. Evidence of disinfection or CIP/SIP to be provided |  |  |  |  |  |  |
|  | - PVC tank used as feed tank of RO plant. There was no record of leachability at time of inspection. |  |  |  |  |  |  |
|  | - No validation record for adequacy of frequency of sanitization RO and DM plant |  |  |  |  |  |  |
| 2. | major |  |  |  |  |  |  |
|  | - No calibration status on pressure gauges at the RO plant and boiler |  |  |  |  |  |  |
| 3. | MINOR |  |  |  |  |  |  |
|  | - Some SOPs were not available at the point of use, especially at Boiler area |  |  |  |  |  |  |
|  | - Equipment usage log sheet found at the time of inspection had no portion for supervisor’s check and approval |  |  |  |  |  |  |
|  | - Procedure for changing micron filter at the post softener section was not strictly adhered to |  |  |  |  |  |  |
| 4. | OTHERS |  |  |  |  |  |  |
|  | - No evidence of cGMP training at the time of inspection. Though, the evidence was said to be at the QA department. |  |  |  |  |  |  |
|  | - The surrounding of the engineering workshop was not well cleaned with cobwebs on the ceilings, floor stained with black oil and office not well arranged. |  |  |  |  |  |  |
|  | - The change room was not tidy enough; it needs to be painted. |  |  |  |  |  |  |
|  | - The toilet was found very dirty, all wall tiles already turned black and the sinks grossly stained. |  |  |  |  |  |  |
|  | - The boiler section was found totally black, probably due to use of black oil. Housekeeping in the area needs to be improved with proper handling of the black oil. |  |  |  |  |  |  |
|  | - Several unwanted scraps of defunct equipment were found littering the engineering workshop area |  |  |  |  |  |  |
|  | - Defunct equipment in the generator house needed to be covered off with appropriate label affixed |  |  |  |  |  |  |
|  | - There was no ETP |  |  |  |  |  |  |
|  | - The title of some SOPs appeared too vague |  |  |  |  |  |  |
|  | - No cleaner was available for water treatment plant |  |  |  |  |  |  |
|  | - The casing of the micron filters at the post softener section should be changed. It has become opaque. |  |  |  |  |  |  |
|  | - The heat level at the MCDP/RO plant is too high |  |  |  |  |  |  |
|  | - Dead leg was observed on water line |  |  |  |  |  |  |