- OBJECTIVE:

To establish the procedure for collection, treatment, monitoring, and disposal of effluents generated from manufacturing and domestic operations to ensure environmental compliance and safety.

- SCOPE:

This SOP applies to all effluent generated from production, quality control laboratories, washing areas, and domestic sources within Biomedical Limited.

- RESPONSIBILITIES/ACCOUNTABILITIES:

Water Treatment Operator: Operate and monitor the effluent treatment plant (ETP).

Engineering Officer: Maintain ETP equipment and pumps.

QC Officer: Conduct analytical testing of effluent parameters.

QA Manager: Review and approve monitoring data.

Factory Manager: Ensure overall compliance and vendor authorization for disposal.

- ABBREVIATION AND DEFINITIONS

PH: Potential of Hydrogen

TSS: Total suspended solid

TSD: Total Dissolved solved

BOD: Biochemical Oxygen Demand

COD: Chemical Oxygen Demand

- PROCEDURES

Domestic Effluent Management

Source of Domestic Effluent:

Domestic effluent includes wastewater generated from toilets, urinals, washrooms, canteens, and staff changing areas.

Collection and Transfer:

  - All domestic wastewater shall be collected via a closed underground drainage system and directed into a primary septic collection tank or sewage holding tank.

  - The drainage system shall be constructed of non-corrosive, chemical-resistant piping with adequate slope to ensure free flow and prevent backflow or stagnation.

  - The septic collection tank shall be periodically de-sludged by a registered waste management contractor licensed by the state environmental protection agency.

- Maintenance and Hygiene Controls:

  - The collection tank shall be inspected weekly by the Engineering or EHS Department for leaks, overflow, or odor nuisance.

  - All domestic effluent tanks shall be fitted with manhole covers and ventilation pipes to prevent anaerobic gas buildup.

  - Routine disinfection using approved biocidal agents (e.g., sodium hypochlorite solution at 0.5–1%) shall be conducted after each desludging activity.

  - Contractors must present valid waste evacuation certificates and disposal manifests, which shall be filed in the Environmental Record Folder under QA supervision.

Safety Measures:

  - Workers involved in desludging must wear chemical-resistant gloves, face masks, boots, and coveralls.

  - Access to the septic area shall be restricted to authorized personnel only.

  - Handwashing and decontamination must be performed immediately after the operation.

Industrial Effluent Treatment

Source of Industrial Effluent:

Industrial effluent includes wastewater from production floors, washing stations, laboratories, equipment cleaning, and other manufacturing-related operations.

Equalization Tank Operation:

  - All industrial wastewater shall be directed to the Equalization Tank where flow variations are balanced.

  - The equalization tank ensures a consistent effluent composition and stable hydraulic load for effective downstream treatment.

  - Activate the raw effluent pump and allow continuous agitation or aeration to maintain uniform mixing.

pH Adjustment and Neutralization

Sampling and Testing:

  - Draw a representative sample of the effluent from the equalization tank and check its pH using a calibrated pH meter.

  - The acceptable pH range before further treatment shall be 6.0 to 9.0.

Chemical Neutralization:

  - If the pH is below 6.0, add Sodium Hydroxide (NaOH) solution gradually while mixing continuously.

  - If the pH is above 9.0, add Citric Acid solution to bring the pH within the neutral range.

  - Ensure slow, incremental dosing to avoid sudden chemical reactions or excessive heat generation.

  - Continue agitation and recheck the pH every 10 minutes until the target range is achieved.

Safety and Controls:

  - Always add chemical to water — never water to concentrated acid or alkali.

  - Handle all chemicals using appropriate PPE (gloves, goggles, respirators, aprons).

  - Keep Material Safety Data Sheets (MSDS) accessible near the treatment area.

Physico-Chemical Treatment

Coagulation and Flocculation Process:

  - Once pH is neutralized, initiate coagulation and precipitation to remove suspended and dissolved solids.

  - Prepare a 1% Alum (Aluminum Sulphate) solution by dissolving 1 kg of alum in 100 liters of clean water in the dosing tank.

  - Operate the dosing pump and inject the alum solution into the effluent stream at a controlled rate to promote floc formation.

  - Mix thoroughly using a mechanical stirrer or aeration pump to ensure uniform dispersion.

Settling and Sludge Separation:

  - Allow the treated effluent to settle for 2–3 hours in the Primary Clarifier Tank or Sedimentation Chamber.

  - The heavier solids and coagulated impurities will settle as sludge at the bottom of the tank.

  - The supernatant (clarified water) shall be decanted carefully into the secondary filtration unit.

Sludge Handling and Disposal:

  - Sludge shall be periodically removed and dewatered using sludge drying beds or filter presses.

  - Dried sludge shall be collected and handed over to a licensed waste disposal contractor for incineration or secure landfill.

  - Maintain a Sludge Disposal Register signed by the QA Officer and vendor representative, indicating date, quantity, and disposal method.

Filtration and Disinfection

- The clarified effluent from the sedimentation tank shall pass through a multi-media filtration system consisting of sand and activated carbon filters.

- Filters shall be backwashed at defined intervals to maintain flow and prevent clogging.

- After filtration, dose the effluent with 1% sodium hypochlorite solution or an equivalent disinfectant to reduce microbial load before final discharge.

- Treated water shall be collected in the Final Holding Tank and re-tested before release.

Monitoring and Compliance Testing

The QC or Environmental Officer shall analyze treated effluent samples for the following parameters:

  - pH: 6.0 – 9.0

  - Total Suspended Solids (TSS): ≤ 100 mg/L

  - Total Dissolved Solids (TDS): ≤ 100 mg/L

  - Biochemical Oxygen Demand (BOD): ≤ 20 mg/L

  - Chemical Oxygen Demand (COD): ≤ 40 mg/L

  - Oil and Grease: ≤ 10 mg/L

- All results shall comply with NESREA Effluent Limit Standards and NAFDAC GMP requirements before discharge to the environment.

- Retain analytical records in the Effluent Monitoring Logbook, duly signed by the QC Analyst and QA Reviewer.

- Monthly summaries of effluent data shall be submitted to management and environmental authorities where required.

- The results shall be documented using the Effluent Water Analytical report (BML.QDG.QA.087-F01).

Preventive Maintenance

- The Engineering Department shall carry out routine inspection, maintenance, and calibration of effluent pumps, pH meters, dosing units, and filtration systems.

- Maintenance activities must be recorded in the ETP Maintenance Logbook with date, technician name, and verification by QA.

- Any deviation or malfunction shall be immediately reported to the QA and EHS departments for corrective action.

Safety and Environmental Protection

- Ensure restricted access to the ETP area with clear hazard signage.

- Provide spill kits, eyewash stations, and fire extinguishers near all chemical storage areas.

- Store neutralizing chemicals in designated ventilated areas away from heat sources.

- Personnel must undergo annual ETP safety and environmental training.

- Periodic internal audits shall be conducted to confirm compliance with WHO, GMP and NAFDAC environmental requirements.

Materials, Equipment, Apparatus and Reagents

Sodium Hydroxide (NaOH)

Citric Acid

Alum (Aluminium Sulphate)

Effluent holding tanks and dosing pumps

pH meter

Filtration system

PPE (gloves, boots, goggles, apron)

- REFERENCE AND ENCLOSURE

ENCLOSURE 1- Effluent Water Analytical report- BML.QDG.QA.087-F01

WHO TRS 961, Annex 6 – GMP for Pharmaceutical Products

NAFDAC GMP Guidelines (2021)

NESREA National Environmental Regulations (2011)

Biomedical Limited Environmental Policy

7.0 TRAINING INVOLVEMENT

| All departmental managers | All sectional heads |
| --- | --- |
| QA Doc. Unit staff | All staff |

8.0 DISTRIBUTION AND CONTROL:

| MASTER COPIES | QUALITY ASSURANCE |
| --- | --- |
| CONTROLLED COPIES | ALL DEPARTMENT |

9.0 CHANGE HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| 00 | Nil | First issue |
| 06 | 05 | - Change in sop format. - Inclusion of traceability of enclosures to parent SOP |