| S.N | AUDIT FINDINGS (OBSERVATION) | ROOT CAUSE ANALYSIS |  | CORRECTIVE ACTION |  | INDICATORS FOR COMPLETION |  | TIMELINE |  | RESPONSIBILITY | CAPA STATUS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CLEAN ROOM |  |  |  |  |  |  |  |  |  |  |  |
| 1 | - Singlet or vest under the clean room garment to be provided | Lack of GMP |  | The singlet or vest will be purchase in bulk and allocated to the staff with a unique tag to individual working in the clean room area and train them on the usage and important of having it on before the overall gown. | 1. Proforma invoice for the proposed purchase 2. SOP on singlet usage in the clean room 3. Training evidence |  | Immediate |  | Admin/ PM |  | Closed |
|  | - Improper usage of secondary change room | Lack of Good house keeping |  | Increase in frequency of cleaning and provision of a big laundry basket | 1. Cleaning chart. 2. picture of the laundry basket |  | Immediate |  | Admin/ QAM |  | Closed |
|  | - Air shower is rusted | Lack of plant preventive maintenance |  | Air shower was replaced with the new one | 1. work order generated for the replacement (work order ref. no.) 2. PPM schedule for the area. |  | Immediate |  | Chief Eng./PM |  | Closed |
|  | - Air shower door Inches has holes to be sealed with silicon | Lack of plant preventive maintenance |  | Air shower door inches was sealed with nonreactive filler | 1. work order generated for the task (work order ref. no.) 2. PPM schedule for the area. |  | Immediate |  | Chief Eng./PM |  | Closed |
|  | - Replacement of coving at the entrance of Filling Room | Lack of plant preventive maintenance |  | The coving will be replaced alongside with the ongoing factory restructuring | Change control for the factory restructuring (Change control number) |  | A month time |  | Chief Eng./PM/QAM |  | Open |
|  | - Improper gowning in the clean room | Lack of GMP |  | A Retraining on gowning procedure in the production to all staff in the clean room area was conducted. | Training evidence |  | immediate |  | PP/PM |  | Closed |
|  | - No Flush Light in Clean Room Corridor | Lack of GMP |  | The flush light has been fixed | Work order number |  | Immediate |  | Chief Eng/PM |  | Closed |
|  | - Faulty Pass-boxes | Lack of routine facility maintenance |  | Faulty pass box will be fix and requalified. | 1. Work order numbers raised. 2. Protocol and report document prepared for the requalification. |  | A week time |  | Chief Eng/PM |  | Open |
|  | - Air Shower to be sprayed | Lack of routine facility maintenance culture |  | The air shower has been sprayed with non-biodegradable paint | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. |  | Closed |
|  | - Discoloration epoxy in the clean room | Lack of routine facility maintenance culture |  | The floor will be repainted with epoxy properties. | Copy of Job order raised |  | A week time |  | PM/Chief Eng. |  | Open |
|  | - No mirror | Lack of GMP |  | A standard mirror for the clean room has been replace for proper check when gowning. | Copy of Job order raised |  | Immediate |  | PM/Chief Eng./Admin |  | Closed |
|  | - No goggles and N195 Nose mask | Lack of GMP |  | Tentatively, the more of the surgical nose mask has been provided for use while the recommended N195 nose mask will be source for. | 1. Nose mask receipt invoice. 2. Copy of proforma invoice on the N195 nose mask brand |  | Immediate |  | PM/PU/Admin |  | Closed |
|  | - Pass boxes not in good condition | Lack of routine facility maintenance |  | Faulty pass box will be fix and requalified. | 1. Work order numbers raised. 2. Protocol and report document prepared for the requalification. |  | A week time |  | Chief Eng/PM |  | Open |
|  | - Leakages in filter holder | Lack of routine facility maintenance |  | Leakage filter holder has been changed and raise a change control for it. | 1. Work order numbers raised. 2. Change control form use. |  | Immediate |  | Chief Eng/PM/DHU |  | Closed |
| BATCH CODING ROOM |  |  |  |  |  |  |  |  |  |  |  |
| 2 | - Cleaning of doors | Lack of good house keeping | Increase in frequency of cleaning with provision of cleaning chart |  |  | 1. Cleaning chart. |  | Immediate |  | Admin/ QAM | Closed |
|  | - External Calibration Label not signed | An oversight | The signed external label has been fixed |  |  | Picture of the label signed label |  | Immediate |  | PM/QAM | Closed |
|  | - No adequate stainless-steel pallets | Lack of GMP | More of the stainless-steel pallets has been ordered for. |  |  | Proforma invoice for the stainless-steel pallet. |  | Two weeks |  | PM/PU/QAM | Open |
|  | - improper arrangement of pouches | Lack of GMP awareness | The pouches have been arranged properly and retraining of the concerned staff done |  |  | Training evidence |  | Immediate |  | PM/PP/QAM | Closed |
|  | - No Separate table for records book and Hand Gloves | Lack of Good housekeeping and GDP | A distinctive area has been provided for both the recording area and keeping of the hand glove. |  |  | Picture of the area showing the separated points for the two tasks |  | Immediate |  | PM/PP | Closed |
|  | - Improper gowning | Lack of GMP | A Retraining on gowning procedure in the production to all staff concerned was conducted. |  |  | Training evidence |  | immediate |  | PP/PM | Closed |
|  | - No artwork samples in the coding room | Lack of GMP | An IPQA officer have been instructed to always ensured the availability of the online coding artwork. |  |  | Copy of the artwork samples for all the products manufacturing in Infusion plant. |  | Immediate |  | PM/QAM | Closed |
|  | - the information board was not used | Lack of GMP | An improvision was made tentatively and a WIP stainless slate will be source for. |  |  | Proforma invoice on the WIP stainless slate |  | Immediate |  | PM/Chief Eng./QAM | Closed |
|  | LOADING AREA |  |  |  |  |  |  |  |  |  |  |
| 3 | - dirty areas (needs to be repainted) | Lack of PPM culture | The areas noted and others seen has been repainted with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Changes of dynamic Pass-box | Lack of GMP | Faulty pass box will be fix and requalified. |  |  | 1. Work order numbers raised. 2. Protocol and report document prepared for the requalification. |  | A week time |  | Chief Eng/PM | Open |
|  | - Trucking pipes not well laid | Lack of factory maintenance/ supervision culture | The exposed trucking pipes has been recovered with new trucking pipes. |  |  | 1. Job order generated for the work. 2. Pictures of ‘before’ and ‘after’ for the laying of the trucking pipes. |  | immediate |  | Chief Eng./PM | Closed |
|  | - Re-painting of rails | Lack of GMP | The rails have been sprayed with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Stands are rusted | Lack of PPM culture | The stands have been sprayed with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Coving of area is not done | Lack of GMP | The coving will be replaced alongside with the ongoing factory restructuring |  |  | Change control for the factory restructuring (Change control number) |  | A month time |  | Chief Eng./PM/QAM | Open |
|  | - Drainage to be repaired | Lack of PPM culture | The drainage part will be fixed alongside with the ongoing factory restructuring |  |  | Change control raised for the factory restructuring (Change control number) |  | A month time |  | Chief Eng./PM/QAM | Open |
|  | - Insecticutor was off at the time of inspection | Lack of Good house keeping | The insecticutors has been fixed |  |  | Work order number raised |  | Immediate |  | Chief Eng/PM | Closed |
|  | - Changing of burnt electrical bulbs | Lack of PPM culture | The burnt bulb has been fixed |  |  | Work order number raised |  | Immediate |  | Chief Eng/PM | Closed |
|  | - Presence of cobwebs | Lack of Good house keeping | An arrangement for the Increase in frequency of cobweb removal was made with provision of long cleaning brush pipe for better removal of cobwebs. |  |  | 1. Cleaning chart. 2. New purchase long cleaning brush pipe. |  | Immediate |  | Admin/ QAM | Closed |
|  | - No adequate tag for “UNSTERILIZED PRODUCTS” | Lack of GMP | A more laminated paper with bold description of “UNSTERILIZED PRODUCT” has been made available for easy identification of product from afar. |  |  | Sample of the laminated A4 paper. |  | Immediate |  | PM/QAM | Closed |
|  | - Improper arrangement of trails and trolleys | Lack of GMP | A distinctive area has been provided for both the trails and trollies. |  |  | Picture of the area showing the separated points for the two. |  | Immediate |  | PM/PP | Closed |
| 4 | MIXING UNIT |  |  |  |  |  |  |  |  |  |  |
|  | - Door to control area in mixing is faulty | Lack of GMP | The door will be properly fix. |  |  | 1. Work order numbers raised. |  | A week time |  | Chief Eng/PM | Open |
|  | - Intercom not working | Lack of PPM culture | The intercom has been fixed by the contractor. |  |  | 1. Work order numbers raised. |  | Immediate |  | Chief Eng/PM/Admin | Closed |
|  | - improper usage of gowns | Lack of GMP | A Retraining on gowning procedure in the production to all staff concerned was conducted. |  |  | Training evidence |  | immediate |  | PP/PM | Closed |
|  | - poor illumination | Lack of PPM culture | The flush light has been fixed there |  |  | Work order number |  | Immediate |  | Chief Eng/PM | Closed |
|  | - Hand Sanitizer not working | Lack of GMP | A hand sanitizer has been provided and |  |  |  |  |  |  |  |  |
|  | - Peeling of epoxy | Lack of routine facility maintenance | The whole spotted area will be repainted with epoxy properties alongside with the ongoing facility restructuring. |  |  | Change control raised for the factory restructuring (Change control number) |  | A month time |  | Chief Eng./PM/QAM | Open |
|  | - No external calibration sticker label on Air Shower door/mixing tanks | An oversight | The signed external label has been fixed |  |  | Picture of the label signed label |  | Immediate |  | PM/QAM | Closed |
|  | - Cleaning of Air shower is inadequate | Lack of Good house keeping | “Cleaning of Air shower” column in the cleaning chart has been added for better monitoring in the cleaning of the air shower. |  |  | 1. Cleaning chart record. |  | Immediate |  | Admin/ QAM | Closed |
|  | - Cleaning of bulbs holder is inadequate | Lack of Good house keeping | An arrangement for the cleaning was immediately done. |  |  | Record of cleaning. |  | Immediate |  | Admin/ QAM | Closed |
|  | - Sketches to be reprinted | Lack of GDP |  |  |  |  |  |  |  |  |  |
|  | - Door inches are rusted | Lack of GMP and PPM culture | The door inches have been sprayed with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - No flush light | Lack of GMP and PPM culture | The flush light has been fixed |  |  | Job order raised form number |  | Immediate |  | Chief Eng/PM | Closed |
|  | - Rusting panel is observed | Lack of GMP and PPM culture | The rusting panel have been sprayed with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Mixing tanks |  |  |  |  |  |  |  |  |  |  |
|  | - Door handle is rusted | Lack of GMP and PPM culture | The door handle has been sprayed with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Spraying of electrical Panel | Lack of in-house contractors Supervision | The paint on the electrical panel were carefully scrap-off and later dusted properly. |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Rusted Weighing Bucket | Lack of GMP | The weighing bucket has been sprayed with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Cleaning of all SOPs | Lack of Good house keeping | Cleaning of the stained laminated SOPs on the wall has been done. |  |  | Routine cleaning chart |  | Immediate |  | PM/QAM/Admin | Closed |
|  | - Open socket | Lack of GMP and PPM culture | The open socket light has been fixed and covered |  |  | Work order number |  | Immediate |  | Chief Eng/PM | Closed |
|  | - UV light holder is dirty to be changed | Lack of GMP and PPM culture | The UV light holder has been changed |  |  | Work order number raised |  | Immediate |  | Chief Eng/PM | Closed |
|  | - No Quantity Label on the bags | Lack of GMP and Good warehouse keeping | The required label on all the sighted bags were label correctly and retrained the staff on Good Manufacturing Practices |  |  | The training evidence |  | Immediate |  | PM/QAM | Closed |
|  | - No Stainless steel stood | Lack of GMP | Stainless steel stood of a GMP specification have been fabricated for use in the unit |  |  | Picture of the stood in the room. |  | Immediate |  | Chief Eng/PM | Closed |
|  | - Replacement of fire extinguisher | Lack of GMP and absence of HSE officer | Expired fire extinguisher will be bought and calibrate. |  |  | Proforma invoice |  | A week time |  | Chief Eng/PM | Open |
|  | - Temperature and relative humidity are high | Lack of GMP | An OOS report has been generated for it and likewise the room remapped. |  |  | 1. filled OOS report 2. The mapping record for the room. |  | Immediate |  | QAM/PM/DHU | Closed |
|  | - The drainage was not covered | Oversight | The drainage has been covered |  |  | Picture of the covered drainage. |  | Immediate |  | PM/PP | Closed |
|  | - Filter integrity tester not yet fixed | Lack of GMP and PPM culture | The frequency of air particulate count and bioburden test for the room has been increased to prevent clogging of the filter while external contractor has been sourced for testing and maintaining the filter. |  |  | 1. Records of those tests from the micro biological laboratory. 2. Contract agreement between BIOMEDICAL and the contractor. |  | Immediate |  | QAM/PM | Closed |
| 5 | AUTOCLAVING AREA |  |  |  |  |  |  |  |  |  |  |
|  | - Spraying of autoclave trolleys | Lack of GMP and PPM culture | The autoclave trolly has been sprayed with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - No SOP on usage of sterilized tags | Lack of GMP | SOP on product offloading from autoclave machine has been reviewed to capture placement of status tag to the arranged product on the trolly |  |  | 1. Reviewed SOP 2. Training evidence 3. Laminated tag |  | Immediate |  | PM/QAM | Closed |
|  | - Repainting of autoclaving area | Lack of GMP and PPM culture | The affected areas have been repainted with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Roof in Pharmalab control room is found dirty | Lack of Good house keeping | An arrangement for the dirty roof was made with provision of long cleaning brush pipe for better removal of cobwebs. |  |  | 1. Cleaning chart. 2. New purchase long cleaning brush pipe. |  | Immediate |  | Admin/ QAM | Closed |
|  | - Incomplete SOP”s | Lack of GDP | Missing control pages has been reprinted and affixed. |  |  | Copy of the full SOP |  | Immediate |  | PM/PP | Closed |
|  | - Patching of wall and Repair of rails | Lack of GMP and PPM culture | The wall and rails has been painted with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Screeding of loading area roof to be done | Lack of Good house keeping | An arrangement for the dirty roof was made with provision of long cleaning brush pipe for better removal of cobwebs. |  |  | 1. Cleaning chart. 2. New purchase long cleaning brush pipe. |  | Immediate |  | Admin/ QAM | Closed |
|  | - Cobwebs at the autoclave area | Lack of Good house keeping | An arrangement for the dirty roof was made with provision of long cleaning brush pipe for better removal of cobwebs. |  |  | 1. Cleaning chart. 2. New purchase long cleaning brush pipe. |  | Immediate |  | Admin/ QAM | Closed |
|  | - Cleaning of autoclave chamber | Lack of Good house keeping | An arrangement for the cleaning was made and cleaning validation was established. |  |  | Cleaning validation protocol and report. |  | Immediate |  | Chief Eng/PM/ QAM | Closed |
|  | - No status on Fire extinguisher | Lack of GMP and absence of HSE officer | Status label for the fire extinguisher has been fix. |  |  | Picture of the label on the fire extinguisher. |  | Immediate |  | QAM/PM | Closed |
|  | - Hole in offloading areas | Lack of GMP and PPM culture | The holes have been filled with required stones. |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Extractors to be fixed | Lack of GMP and PPM culture | The bad extractor has been repaired. |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Re-painting of rails | Lack of GMP and PPM culture | The rails have been painted with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Cutting of unused pipes | Lack of GMP and PPM culture | The unused pipes have been carefully cut and filled up with necessary stone and painted with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - No chair was used for demarcation as at the time of inspection | Oversight | The chair that served as crossover bench has been placed for proper demarcation. |  |  | Picture of the chair |  | Immediate |  | PM/PP | Closed |
|  | - Unused pipes to be cut off | Lack of GMP and PPM culture | The unused pipes have been carefully cut and filled up with necessary stone and painted with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
| 6 | OFFLOADING UNIT |  |  |  |  |  |  |  |  |  |  |
|  | - No adequate tag for “STERILIZED PRODUCTS” | Lack of GMP | SOP on product offloading from autoclave machine has been reviewed to capture placement of status tag to the arranged product on the trolly |  |  | 1. Reviewed SOP 2. Training evidence 3. Laminated tag |  | Immediate |  | PM/QAM | Closed |
|  | - Improper arrangement of sterilized products | Lack of GMP | The concerned staff were retrained on Good Manufacturing Practices |  |  | Training evidence |  | Immediate |  | PM/QAM | Closed |
|  | - Improper arrangement of trolleys/trays | Lack of GMP | The concerned staff were retrained on Good Manufacturing Practices |  |  | Training evidence |  | Immediate |  | PM/QAM | Closed |
|  | - Roof leakages at offloading area | Lack of GMP and PPM culture | The leaking roof has been fixed |  |  | Picture of the new fixed roof |  | Immediate |  | PM/QAM | Closed |
| 6 | PACKING UNIT |  |  |  |  |  |  |  |  |  |  |
|  | - Leakage testing machine not working | Lack of GMP | A change control was raised for the changes in the validated procedure and the bad leak testing machine has been tag “UNDER maintenance” and more of contract staff were dedicated to do a manual leakage testing. Also, |  |  | 1. change control record 2. Job order raised. |  | Immediate |  | Chief Eng/QAM/PM | Closed |
|  | - No waste basket | Lack of GMP and Good house keeping | A new basket was procured for waste generated during packing |  |  | Invoice and requisition note raised |  | Immediate |  | PP/Admin | Closed |
|  | - Temperature Mapping | Lack of GMP | A protocol and report for the mapping will be generated alongside with the ongoing facility restructuring |  |  | 1. Change control for the facility restructuring. 2. Protocol and Report documents |  | Four weeks to this time |  | QAM/PM/DHU | Open |
|  | - Poor illumination | Lack of GMP | The well illuminating flush light was fixed |  |  | Work order number |  | Immediate |  | Chief Eng/PM | Closed |
|  | - No Rejects room | Lack of GMP | Provision of reject room have been made alongside with the ongoing restructuring. |  |  | Change control for the facility restructuring. |  | Four weeks to this time |  | QAM/PM/Chief Eng | Open |
|  | - Peeling of epoxy | Lack of routine facility maintenance | The whole spotted area will be repainted with epoxy properties alongside with the ongoing facility restructuring. |  |  | Change control raised for the factory restructuring (Change control number) |  | A month time |  | Chief Eng./PM/QAM | Open |
|  | - Cleaning is inadequate | Lack of Good house keeping | The frequency of cleaning has been increased and monitored. |  |  | 1. Cleaning chart. |  | Immediate |  | Admin/ QAM | Closed |
|  | - rusting panel | Lack of GMP and PPM culture | The rusting panel have been sprayed with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Tightening of the conveyor belt in packing line | Lack of GMP and PPM culture | The belt has been tightened and fixed |  |  | Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - No enough stainless chairs | Lack of GMP | Stainless steel stood of a GMP specification have been fabricated for use in the unit |  |  | Picture of the stood in the room. |  | Immediate |  | Chief Eng/PM | Close |
|  | - No cleaned utensil room |  |  |  |  |  |  |  |  |  |  |
| 7 | WALKWAY 2 (Corridor to Mr. Godwin Office) |  |  |  |  |  |  |  |  |  |  |
|  | - Coving of the corridor not yet done | Lack of GMP | Provision for the cleaned utensil room have been made alongside with the ongoing restructuring. |  |  | Change control for the facility restructuring. |  | Four weeks to this time |  | QAM/PM/Chief Eng | Open |
|  | - Insectrocutor not working | Lack of Good house keeping | The insecticutors has been fixed |  |  | Work order number raised |  | Immediate |  | Chief Eng/PM | Closed |
|  | - Exposed pipe hole | Lack of GMP and PPM culture | The holes have been filled with required stones. |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - unsmooth area | Lack of GMP and PPM culture | The unsmooth area has been filled with required stones. |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Blocking of exposed wall surface | Lack of GMP and PPM culture | The exposed wall have been filled with required stones. |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Poor Illumination (Changing of Bulb) | Lack of GMP and PPM culture | The poor light has been fixed |  |  | Work order number |  | Immediate |  | Chief Eng/PM | Closed |
|  | - Presence of ants | Lack of GMP | An increase in in-house fumigation was recommended and environmental monitoring test was arranged for microbial load in the air before an inhouse fogging was arranged. |  |  | 1. Copy of the test record done 2. fogging memo |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - No adequate signage | Lack of GMP | Proper signage has been put in place and laminated for use. |  |  | Laminated tags |  | Immediate |  | PM/QAM | Closed |
| 8 | FIRST AID UNIT |  |  |  |  |  |  |  |  |  |  |
|  | - Improper arrangement of drugs | Lack of GMP and Good house keeping | The drugs have been arranged |  |  | Picture of the shelve |  | Immediate |  | PM/QAM | Closed |
|  | - The place in not tidy | Lack of GMP and Good house keeping | The place has been arranged |  |  | Picture of the shelve |  | Immediate |  | PM/QAM | Closed |
| 9 | PHARMACIST OFFICE |  |  |  |  |  |  |  |  |  |  |
|  | - Improper arrangement of records | Lack of GDP and Good house keeping | The shelve have been arranged |  |  | Picture of the shelve |  | Immediate |  | PM/QAM | Closed |
|  | - No shelve (littering of BMR on the floor) | Lack of GMP and Good house keeping | The documents have been arranged in the provided carton |  |  | Picture of the carton |  | Immediate |  | PM/QAM | Closed |
| 10 | VISITORS CHANGE ROOM |  |  |  |  |  |  |  |  |  |  |
|  | - Re-painting of the wall | Lack of routine facility maintenance culture | The wall has been repainted with non-biodegradable paint |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Reduction of the length of cross over bench | Lack of GMP | The cross over bench has been reduced to fit the area mentioned |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Hygrometer chart not updated | Lack of GMP | A deviation report has been generated for it and the chart has also been updated accordingly. |  |  | 1. filled deviation report |  | Immediate |  | QAM/PM/DHU | Closed |
|  | - Cobwebs in visitors change room and Access control room | Lack of Good house keeping | An arrangement for the cleaning of the cobwebs was made with provision of long cleaning brush pipe for better removal of cobwebs. |  |  | 1. Cleaning chart. 2. New purchase long cleaning brush pipe. |  | Immediate |  | Admin/ QAM | Closed |
|  | - Repair of door | Lack of GMP and PPM culture | The door has been repaired |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Changing of Electrical fuse | Lack of GMP and PPM culture | The electrical fuse has been replaced with new one |  |  | Work order number |  | Immediate |  | Chief Eng/PM | Closed |
|  | - Access control door not working | Lack of GMP and PPM culture | The electrical panel making it malfunction has been fixed. |  |  | Work order number |  | Immediate |  | Chief Eng/PM | Closed |
|  | - Changing of door bolts at the clean room entrance | Lack of GMP and PPM culture | The door bolts have been changed repaired |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - Poor illumination | Lack of GMP and PPM culture | The poor light has been fixed |  |  | Work order number |  | Immediate |  | Chief Eng/PM | Closed |
|  | - No hand sanitizer at the entry of clean room | Lack of GMP | The hand sanitizer dispenser has been provided and station for frequent usage by the concerned staff |  |  | Proforma invoice |  | Immediate |  | PM/Admin | Closed |
|  | - The shoe rack is damaged | Lack of GMP | The shoe rack has been repaired and station for usage for the concerned staff |  |  | Picture of the repaired shoe rack |  | Immediate |  | PM/Admin | Closed |
| 11 | CLOAK ROOM (MALE AND FEMALE) |  |  |  |  |  |  |  |  |  |  |
|  | - No Insectrocutor at the entrance of both male and female cloak room | Lack of Good house keeping | An insecticutors has been fixed to serve both cloak rooms |  |  | Work order number raised |  | Immediate |  | Chief Eng/PM | Closed |
|  | - No Hanger not provided | Lack of GMP and Good house keeping | More of cloth hanger has been provided to both cloak room for staff usage. |  |  | Picture of the hangers. |  | Immediate |  | PM/Admin | Closed |
|  | - Dedicated locker for personal belongings is not adequate | Lack of GMP and Good house keeping | The lockers have been labelled appropriately for usage. |  |  | Picture of the labeling. |  | Immediate |  | PM/Admin | Closed |
|  | - No proper labelling of waste bin | Lack of GMP and Good house keeping | The waste bin has been labelled appropriately for usage. |  |  | Picture of the labeling. |  | Immediate |  | PM/Admin | Closed |
|  | - No Cross over bench | Lack of GMP | The cross over bench has been fabricated to fit the area mentioned |  |  | Copy of Job order raised |  | Immediate |  | PM/Chief Eng. | Closed |
|  | - No signage (Male/Female Change room) | Lack of GMP | Proper signage has been put in place and laminated for use. |  |  | Laminated tags |  | Immediate |  | PM/QAM | Closed |
|  | - The drainage in the bathroom not well channeled (partitioning) | Lack of plant preventive maintenance | Channeling of the drainage will be partitioned alongside with the ongoing factory restructuring |  |  | Change control for the factory restructuring (Change control number) |  | A month time |  | Chief Eng./PM/QAM | Open |
|  | - Poor usage of garments | Lack of GMP | A Retraining on gowning procedure in the production to all staff concerned was conducted. |  |  | Training evidence |  | immediate |  | PP/PM | Closed |
|  | - No thorough supervision of the cloak room | Lack of GMP | A Retraining on factory entrance procedure in the production to all staff concerned was conducted. |  |  | Training evidence |  | immediate |  | PP/PM | Closed |
|  | - No mirror | Lack of GMP | A mirror has been provided for proper gowning |  |  | The mirror invoice and picture |  | immediate |  | PP/PM | Closed |
|  | - No proper pictorial diagram for gowning | Lack of GMP | A pictorial representative for gowning procedure has been printed on A4 paper and laminated for use. |  |  | Copy of the laminated pictures |  | immediate |  | PP/PM | Closed |
| 12 | GENERAL |  |  |  |  |  |  |  |  |  |  |
|  | - No CCTV | Lack of HSE officer | Installation of CCTV cameral is currently part of the ongoing restructuring. |  |  | Change control for the factory restructuring (Change control number) |  | A month time |  | Chief Eng./PM/QAM | Open |
|  | - No adequate signage such as do not touch the wall, pull, push, mind your step, first aid unit etc | Lack of GMP | Proper signage has been put in place and laminated for use. |  |  | Laminated tags |  | Immediate |  | PM/QAM | Closed |