- OBJECTIVE:

To provide written guidelines for Effluent treatment plant.

- SCOPE:

This SOP covers the written procedure for Effluent treatment plant.

- RESPONSIBILITIES/ACCOUNTABILITIES:

Water treatment officer, Engineering Officer, Quality Control Officer, Quality Assurance Manager, Superintendent Pharmacist/Factory Manager.

- ABBREVIATION AND DEFINITIONS

PH: Potential of Hydrogen

TSS: Total suspended solid

TSD: Total Dissolved solved

BOD: Biochemical Oxygen Demand

COD: Chemical Oxygen Demand

- PROCEDURES

Domestic Effluent:

- Domestic effluent from the toilets and urinals is received to the septic tank collection tank by a registered contractor.

Industrial Effluent:

- Check the raw effluent Ph from the equalization tank and add the neutralizing chemical, Sodium Hydroxide (NaOH)/ citric Acid till the ph 6.5-9.0

- Switch “ON” the raw effluent pump and allow the effluent to mix with in the Equalization tank continuously.

- Take sample from the chamber of the tank and check the PH if it is within the specifications

- Add NaOH if the effluent sample is low i.e <6

- Add citric acid if the effluent sample has a high Ph >9

- Switch the pump on and mix again

Physio-Chemical Treatment:

- The physio-chemical treatment process includes neutralizing, chemical coagulation and precipitation.

- Chemical Preparation.

- Prepare the 1% alum in the tank.

- 1% Alum: 1kg of alum dissolved per 100 litres of Solvent

- Operate the Dosing pump

- Dose the prepared Alum into the effluent tank

- The effluent after adjusting PH, allowed to settle then the settled sludge at the bottom shall be evacuated by the registered contractor (Sludge handling system).

- Collect the effluent water and check

- Parameters like PH, TSS, TDS, COD, BOD, Oil and grease etc shall be analyzed.

- The effluent water shall meet the following parameter,

Materials, Equipment, Apparatus and Reagents

NaOH - Sodium Hydroxide

- REFERENCE AND ENCLOSURE

- IN-HOUSE

7.0 TRAINING INVOLVEMENT

| Engineering Manager | QC Head |
| --- | --- |
| QA Doc. Unit staff | Water treatment officer/QC Staff |

8.0 DISTRIBUTION AND CONTROL:

| MASTER COPIES | QUALITY ASSURANCE |
| --- | --- |
| CONTROLLED COPIES | ALL DEPARTMENT |

9.0 CHANGE HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| 00 | Nil | First issue |
| 06 | 05 | - Change in sop format. - Inclusion of traceability of enclosures to parent SOP |