- OBJECTIVE:

This SOP describes the method of sanitization of the Reverse Osmosis Machine.

- SCOPE:

To provide for the sanitization of Reverse Osmosis machine (R.O)

- RESPONSIBILITY/ACCOUNTABILITY:

Water Treatment Officer, Technical Officers, Quality Control Chemist, Microbiologist, Technical Manager, Quality Assurance Manager and the Superintendent Pharmacist

- ABBREVIATIONS AND DEFINITIONS:

RO – Reverse Osmosis Machine

- PROCEDURE:

-      Clean the inner part of the cartridge filter casing

-      Replace all the cartridge filters before sanitization commences

- Ensure valve 2,3,4 is opened

- Ensure valve 1,5,6 is closed

- Ensure the drain line is closed

- Fill 70Ltr of water into the sanitization tank and add approximately 250ml of Hydrogen peroxide into the water.

- Turn-on the main switch

- Start the permeate water pump

- Start the salty water pump

- Allow the solution to circulate for 25minute

- Allow contact time of 40min

- Drain the solution from the sanitization tank

- Fill up the sanitization tank with fresh RO water and recycle for 25 minutes.

- Return the RO valve to normal operation mode and flush for 20minutes.

- Take a sample of the water after flushing and ensure it conforms to the specifications on the checklist e.g. Conductivity, pH, Hardness etc.

TEST CONDUCTED:

-	Chemical Analysis of the water is carried out for the following:

| - Parameter | Limit |
| --- | --- |
| - Acidity / Alkalinity | < 0.1ml NaOH /< 0.15ml HCl is consumed |
| - Degree of hardness | < 5 PPM |
| - Chloride | < 0.5 PPM |
| - pH | 5.0 – 7.0 |

The final rinse water must comply with requirements for water for injections BP 2002

CONCLUSION:

-	Reverse Osmosis Machine is certified for processing water into the steam jacket WFI tank.

REQUIRED MATERIALS:

- Citric Acid or Hydrogen Peroxide

FREQUENCY

2 weeks

Safety, Health and Environmental Precautions:

-		Always be appropriately dressed when carrying out any procedure

- REFERENCE/ENCLOSURE:

In-house

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |