- OBJECTIVE:

To provide the method for Cleaning and sanitization of raw water tanks purified water storage tanks, reverse osmosis storage tank and water for injection storage tanks.

- SCOPE:

This SOP covers the procedure to follow while cleaning and sanitizing of water storage tanks.

- RESPONSIBILITY/ACCOUNTABILITY:

- Water treatment operator/water treatment officer shall be responsible for the execution of this procedure.

- Engineering head shall be responsible for the implementation of this SOP.

- Head QA/Designee shall be responsible for the compliance of this SOP.

- ABBREVIATIONS AND DEFINITIONS:

SOP: standard operating procedure

QA: quality assurance

RO:  reverse osmosis machine

- PROCEDURE:

- Put the “UNDER CLEANING” board on the water storage tank and inform necessary personel.

- Open the tank cover and drain out all the water in the water storage tank from the drain point.

- Personnel responsible for cleaning should only be allowed to enter into the tank after taking their bath and washing their hands and feet thoroughly.

- Clean the walls and floor of the tank with soft plastic scrubber and clean towel thoroughly.

- Flush the tank with reverse osmosis machine water for about 10 minutes and ensure that the tank drain valve remain open.

- Prepare 1kg of citric acid and dilute with 20ltr of water to wash the inner part.

- Clean the inside of the tank with the solution of citric acid and water and scrub thoroughly.

- Rinse thoroughly after scrubbing, continue rinsing the tank thoroughly (in and out) with RO water

- Drain out the solution

- Remove the ‘’UNDER CLEANING’’ board and cover the tank.

- Take a sample of newly processed water and and ensure it conforms with the specifications on the checklist e.g. Conductivity, Ph, Hardness e.t.c.

- Give sample of wash for analysis to QC for analysis

- Clean water storage tanks every 2 weeks respectively as stated in the water storage cleaning schedule checklist.

Materials, Equipment

- Citric acid

- plastic scrubber

- Towel

- RO (Reverse osmosis) water

- REFERENCE/ENCLOSURE:

In-house

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |