- OBJECTIVE:

To provide the instructions for the operating UV water sterilizer.

- SCOPE:

To provide written guidelines for the operating UV water sterilizer.

- RESPONSIBILITY/ACCOUNTABILITY:

Water treatment office, Q.A. Officer, Microbiologist, Production Pharmacist.

- ABBREVIATIONS AND DEFINITIONS:

N/A

- PROCEDURE:

- To avoid the machine falling down use clips to hold it up in a horizontal position (wall mounted)

- Plug the UV light tube into the blaster which has 4 sockets and then insert through the nut

- Connect water inlet and outlet to the water supply. Visually inspect for leakages and do not proceed until any leakages found have been resolved

- A warning beep sound will be heard and the indicator light will be seen if there has been any damage to the UV lamp

- The filter placed before the UV lamp must be 0.5 micron and taps must be present to allow QC to take samples for microbiological analysis

Operation:

- Switch on the lamp at the beginning of the production day and ensure that it is on once water treatment has commenced

- The UV lamp is guaranteed for 8,000 hours and it should be replaced every 12 months or when its faulty.

Cleaning:

- Shut down the power, take out the UV tube, and unscrew the nuts on both sides.

- Take out the quartz tube, clean the tube and the body using IPA, DM water and cotton wool.

- Use IPA to wipe the tube after it has been cleaned and always check for leakages after installation

- This should be done every 2 weeks.

Maintenance:

- Do not look directly at the UV lamp while the device is functioning as it will hurt the eyes

- Add a one-way valve if the water pressure will be higher than 3kg

- The quartz tube should be cleaned as instructed

- The filters must be changed regularly

- If the UV tube does not light does not light up check if the power indicator has been turned on/off, if it is on and not lit the replace the fuse, if this is done and  it is still unlit and a beeping sound is heard then the UV tube needs to be changed

- Water leakages should be addressed thus:

- If there is water on either side of the nuts, change the rubber

- If there is leakage in the tube, check the quartz tube and replace if damaged

- If there are leakages at the water IN/OUT section, shut down water supply, unfasten the connecter and put some water proof tape in the connecter and then replace

Attention: to prevent damage to the retina’s always wait a full 2 minutes before changing the tube after turning the power off

- REFERENCE/ENCLOSURE:

In-house

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |