- OBJECTIVE:

To provide the method of De- scaling multi column distillation plant.

- SCOPE:

To provide written guidelines for De- scaling multi column distillation plant.

- RESPONSIBILITY/ACCOUNTABILITY:

Water treatment Operator/Officer, Engineer, Q.C Chemist.

- ABBREVIATIONS AND DEFINITIONS:

MCDP – Multi Column Distillation Plant

- PROCEDURE:

- Detach all the pneumatic valves, sensors, air –vent, purging valves, conductivity sensors.

- Add 2000 litres of distilled water into the MCDP feed tank and add 15kg of caustic soda, stir     homogeneously.

- Turn on the MCDP main switch.

- Turn on the feed water pump manually and circulate the caustic soda solution for 4 hours.

- Drain out the solution.

- Give contact time of 3 hours

- Flush the system with fresh water.

- Fill 2000 litres of distilled water into the feed tank and add 15 litres of hydrochloric acid

- Circulate the mixture for 4 hours.

- Drain out the solution.

- Give contact time of 3 hours.

- Connect a source of water to the feed tank and circulate through the MCDP for 5 hours for            	flushing.

- Connect back all the detached devices.

- Test-run the MCDP in manual mode and also check the quality of the water as per SOP standard.

- Take a sample of newly processed water and ensure it conforms with the specifications on the                      	checklist e.g. Conductivity, pH, Hardness etc.

- Give sample of water to QC for analysis

- REFERENCE/ENCLOSURE:

In-house

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |