- Objective:

To provide written guidelines for Calibration of Booth.

- Scope:

This SOP covers the procedure for Calibration of the Booth.

- Responsibility/accountability:

Laboratory Assistance, Quality Control Chemist, Quality Control Microbiologist, Quality Assurance Manager, Supt. Pharmacist.

4.0 Abbreviations and Definitions

N/A

- Procedure

- Ensure the booth is thoroughly cleaned with lint-free cloth dampened with soapy water and then IPA.

- Plug the Booth to the power mains.

- Put on the booth, then the functional buttons, and allow it to stand for one hour before commencing the activity.

- Using a lux meter, take the luminosity at the work area. Record these values.

- Using the polyethylene, observe if there is blow and suction across the device. Take readings with an anemometer for air velocity.

- With the aid of the fog generator containing the in-house fog solution, demonstrate suction for the booth area.

- Take recordings where necessary and save evidence of performance verification.

- With the aid of a particle counter, take data for non-viable particle count in operation and at rest.

- Take the active and passive air bio burden for the booth area. Have at least three datasets for this step.

Materials, Equipment, Apparatus and Reagents

Lux meter

Anemometer

Fogger machine

Safety, Health and Environment Precautions

Wear appropriate PPE

- REFERENCE/ENCLOSURE

IN-HOUSE

- TRAINING INVOLVEMENT

| All departmental managers | All sectional heads |
| --- | --- |
| QA Doc. Unit staff |  |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | QUALITY ASSURANCE |
| --- | --- |
| CONTROLLED COPIES | ALL DEPARTMENT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REVIEW DATE | REASON FOR REVIEW |
| --- | --- | --- | --- |
| ### 00 | ### Nil | ### Nil | First |
| ### 01 | ### 00 | ### Jan 2024 | - Inclusion of enclosures format - Change in sop format generally |