| S.N | AUDIT FINDINGS (OBSERVATION) | ROOT CAUSE ANALYSIS | CORRECTIVE ACTION | INDICATORS FOR COMPLETION | TIMELINE | RESPONSIBILITY | CAPA STATUS |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CRITICAL |  | ENGINEERING |  |  |  |  |  |
| 1 | - WFI storage tank was observed to be washed manually with no evidence of disinfection after such process of washing. Evidence of disinfection or CIP/SIP to be provided | Lack of GMP/GDP | A procedure to indicate the process of washing, maintenance and frequency has been developed. The WFI storage tank has also been included into the Plant Preventive Maintenance (PPM) schedule for proper monitoring and documentation. | The SOP on WFI storage tanks maintenance. PPM schedule showing the WFI storage tank inclusion. | 3weeks time | Chief Eng./DUH | Open |
|  | - PVC tank used as feed tank of RO plant. There was no record of leachability at time of inspection. | Lack of GDP | The certificate on the leachability done externally is always domicile with QA documentation unit and shall always be available when next we have audit. | Copy of the last leachability test done on the PVC tank. | Immediately | Chief Eng. | Closed |
|  | - No validation record for adequacy of frequency of sanitization RO and DM plant | Lack of GMP | A protocol and report for the validation on both the RO and DM plant will be generated. | The protocol with BML/VAP/ENG/24/XXX and report BML/VAR/ENG/24/XXX developed for the whole water plant as stated in the SOP of Validation procedure BML-QDG-QA-111 | 4weeks time | Chief Eng/QAM | Open |
| 2. | MAJOR |  |  |  |  |  |  |
|  | - No calibration status on pressure gauges at the RO plant and boiler | Oversight | Calibration status has been put on the pressure gauges at the RO and Boiler for easy identification | Picture of the calibration label pasted on the RO and Boiler done. | Immediately | Chief Eng. | Closed |
| 3. | MINOR |  |  |  |  |  |  |
|  | - Some SOPs were not available at the point of use, especially at Boiler area | Lack of GMP | All the SOPs on each of the equipment and processes has been arranged and hang closed to its equipment for operator use. | List of Engineering SOPs showing the title of all the SOPs in the engineering with the inclusion of their validity. | Immediately | Chief Eng./DHU | Closed |
|  | - Equipment usage log sheet found at the time of inspection had no portion for supervisor’s check and approval | Lack of GMP | The equipment logbook will be review with its SOP to capture the format showing the portion for the supervisor check and approval in the body of the SOP as stated in our new SOP of SOP BML-QDG-QA-001 for the facility. | The change control BML/CC/QDG/24/001 raised for the review of all SOP in the facility. | 3weeks time | Chief Eng. | Open |
|  | - Procedure for changing micron filter at the post softener section was not strictly adhered to | Lack of GMP | The procedure on the changing of micron filter at the softener section in at the water system unit of the factory will henceforth be adhere to and the operator has been retrained on the important of following the procedure as stated. | Individual training attendant on the procedure. | Immediately | Chief Eng. | Closed |
| 4. | OTHERS |  |  |  |  |  |  |
|  | - No evidence of cGMP training at the time of inspection. Though, the evidence was said to be at the QA department. | Oversight | Evidence of training as reiterated domicile with the QA documentation unit. | The copy of the training done so far. The training matrix schedule for 2024 showing the detail of engineering training topics. | Immediately | Chief. Eng | Closed |
|  | - The surrounding of the engineering workshop was not well cleaned with cobwebs on the ceilings, floor stained with black oil and office not well arranged. | Lack of good house keeping | The surrounding has been cleaned jointly with the housekeepers and signed the checked record by an engineering officer to show the completion of the cleaning. | Chart/record of cleaning by the housekeeper provided for the area. | Immediately | Chief Eng/HSE officer | Closed |
|  | - The change room was not tidy enough; it needs to be painted. | Lack of good housekeeping and PPM | The room has been cleaned and painted with nonbiodegradable paint. The area including the whole building has been included in the PPM schedule for the facility. | Picture of the old and new area painted. The PPM schedule showing the facility maintenance. | Immediately | Chief Eng/QAM | Closed |
|  | - The toilet was found very dirty, all wall tiles already turned black and the sinks grossly stained. | Lack of good housekeeping and PPM | The room has been cleaned and painted with nonbiodegradable paint. The area including the whole building has been included in the PPM schedule for the facility. | Picture of the old and new area painted. The PPM schedule showing the facility maintenance. | Immediately | Chief Eng/QAM | Closed |
|  | - The boiler section was found totally black, probably due to use of black oil. Housekeeping in the area needs to be improved with proper handling of the black oil. | Lack of good house keeping | The surrounding has been cleaned jointly with the housekeepers and signed the checked record by an engineering officer to show the completion of the cleaning. | Chart/record of cleaning by the housekeeper provided for the area. | Immediately | Chief Eng/HSE officer | Closed |
|  | - Several unwanted scraps of defunct equipment were found littering the engineering workshop area | Lack of good house keeping | The surrounding has been cleaned jointly with the housekeepers and most of the scraps have been moved and well-arranged into the engineering workshop | Chart/record of cleaning by the housekeeper provided for the area. | Immediately | Chief Eng/HSE officer | Closed |
|  | - Defunct equipment in the generator house needed to be covered off with appropriate label affixed | Lack of GMP | The equipment not in use has been properly label and covered with polythene bag. | The picture of the label ‘NOT IN USE’ affixed on them. | Immediately | Chief Eng. | Closed |
|  | - There was no ETP | Lack of GMP | The records for an improvised Effluent Treatment Plant (ETP) is available and always monitored, sampled and generate a records for regulators by the quality control unit of the facility. | Records of results by the Quality Control unit of Quality department. Copies of records submitted to the regulatory bodies. | Immediately | Chief Eng/QAM | Closed |
|  | - The title of some SOPs appeared too vague | Lack of GDP | The affected SOPs will be reviewed to remove any ambiguities in the written of the SOPs | The change control BML/CC/QDG/24/001 raised for the review of all SOP in the facility. | 3weeks time | Chief Eng. | Open |
|  | - No cleaner was available for water treatment plant | Lack of Goodhouse keeping | A housekeeper has been assigned for routine cleaning of the area. | Chart/record of cleaning by the housekeeper provided for the area. | Immediately | Chief Eng/HSE officer | Closed |
|  | - The casing of the micron filters at the post softener section should be changed. It has become opaque. | Lack of GMP | The casing has been changed for the micron filter. The changing due to its validation has been included in the PPM schedule for the facility. | Picture of the old and new area filter. The PPM schedule showing the inclusion of the micron filter on the water plant. | Immediately | Chief Eng/QAM | Closed |
|  | - The heat level at the MCDP/RO plant is too high | Lack of GMP | The MCDP/RO at the water plant has been included into the ongoing facility restructuring. | The change control BML/CC/ENG/24/001 raised for the review of all SOP in the facility. | October 2024 | Chief Eng./ED | Open |
|  | - Dead leg was observed on water line | Lack of GMP | The part having deadleg will be removed carefully during this ongoing facility restructuring by the engineer on site and chemically treated for the removal of surface contamination of the changed pipe. | The change control BML/CC/ENG/24/001 raised for the review of all SOP in the facility. | October 2024 | Chief Eng./ED | Open |