BIOMEDICAL LIMITED

# INSTALLATION QUALIFICATION (IQ)

# PROTOCOL

# FOR

# IVEN DYNAMIC PASS BOX

EQUIPMENT SR. NO. –

EQUIPMENT ID. –

LOCATION – INFUSION FACTORY FILLING ROOM AREA

PROTOCOL No. – BML/PDF/FA/PT/26/001

PROVIDED BY:

BIOMEDICAL LIMTED

KWARA STATE, NIGERIA

# TABLE OF CONTENT

Cover Page											1

Table of content										2

Protocol Format Approval Sheet								3

Objective											4

Scope											5

Responsibilities and Qualification team							5

Equipment Identification and Description							5-6

Prerequisite										6

Abbreviations and definitions								6

References											7

Equipment installation Checklist								7-9

Installation Qualification Report								10

Deviation Report										11

Conclusion											12

List of attachments										12

Report Approval										13

- PROTOCOL FORMAT APPROVAL:

Signatures in this page indicate that this document and its format have been prepared, checked and approved by the personnel concerned. It shall be signed and dated as shown below.

|  | WRITTEN BY: | REVIEWED BY: |
| --- | --- | --- |
| Signature |  |  |
| Position |  |  |
| Date |  |  |

|  | APPROVED BY: | AUTHORISED BY: |
| --- | --- | --- |
| Signature |  |  |
| Position |  |  |
| Date |  |  |

2.0 OBJECTIVE

The purpose of the study is to ensure proper installation of the fourteen IVEN DYNAMIC PASS BOX at THE FILLING ROOM AREA (FA), INFUSION FACTORY, BIOMEDICAL LIMITED.

This study verifies:

- Qualification of the equipment, installation and to ensure that all background information is performed to assure conformance to BIOMEDICAL LIMITED and manufacturer’s specifications.

- The equipment meets the current good manufacturing practices requirements and all other regulatory obligations

- No unauthorized or unrecorded modifications have taken place.

- Operation procedures/preventive maintenance procedures have been identified and listed.

- All critical instrumentation have been identified

- All utilities are properly connected

- All safety features are accounted for

- All relevant data obtained have been checked

3.0 SCOPE

- This protocol is applicable in carrying out the installation qualification of the fourteen Dynamic Pass box at the Infusion manufacturing site, Biomedical Limited, Kwara State.

- To be performed after the completion of the design qualification

- To be performed at the time of relocation.

4.0 RESPONSIBILITIES AND QUALIFICATION TEAM

The following departments shall be involved in:

| DEPARTMENT | RESPONSIBILITY |
| --- | --- |
| Engineering Team | Provision of needed utility and machine installation |
| Head Of Engineering | Review of the Installation Qualification Document |
| QA –Manager | Final Documentation and system acceptability |
| Superintendent Pharmacist/factory Manager | Authorization |

The following personnel will be involved in the execution of the Qualification

| S/No. | DEPARTMENT | NAME | SIGNATURE |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |

5.0 EQUIPMENT IDENTIFICATION AND DESCRIPTION

IDENTIFICATION

| Equipment Name | IVEN DYNAMIC PASS BOX |
| --- | --- |
| Manufacturer’s Name | SHANGAI IVEN PHAMATECH ENGINEERING CO. LTD (CHINA) |
| Supplier’s name | SHANGAI IVEN PHAMATECH ENGINEERING CO. LTD (CHINA) |
| Location of Installation | FILLING ROOM AREA (INFUSION FACTORY) |

DESCRIPTION:

………………………………………………………………………………………………………………………………………………..………………………………………………………………………………………………………………………………………………..

………………………………………………………………………………………………………………………………………………..

………………………………………………………………………………………………………………………………………………..

………………………………………………………………………………………………………………………………………………..

………………………………………………………………………………………………………………………………………………....................................................................................................................................……………..

6.0 PREREQUISITE

The equipment shall confirm the specifications and requirements as specified in the Design Qualification

| S/N | ACCEPTANCE CRITERIA |
| --- | --- |
| 1 | User Requirement specification |
| 2 | Design Qualification |

7.0 ABBREVIATIONS AND DEFINITIONS

| Abbreviation | Definition |
| --- | --- |
| SOP | Standard Operating Procedure |
| MOC | Material of Construction |
| HMI | Human Machine Interface |
| ENGR | Engineering |
| IQ | Installation Qualification |
| QA | Quality Assurance |
| VAC | Voltage Alternating Current |
| S. S | Stainless Steel |
| LTD | Limited |
| V | Voltage |
| GMP | Good manufacturing practices |
| AC | Alternating Current |
| Amps | Ampere |
| W | Watt |
| VDC | Voltage Direct Current |
| DC | Direct Current |
| MCB | Miniature Circuit Breaker |
| KW | Kilowatt |
| PLC | Programmable Logic Control |

8.0 REFERENCES:

The list of reference documents, which are referred for preparation and review of this document, is as follows: -

- S.O.P for Installation, Operation & Performance Qualification of equipment & Instrument: BML-QDG-QA-111

- Machine Manual supplied by SHANGAI IVEN PHAMATECH ENGINEERING CO. LTD

- Design Qualification supplied by SHANGAI IVEN PHAMATECH ENGINEERING CO. LTD

9.0 EQUIPMENT INSTALLATION CHECKLIST:

Pre-Installation Consideration

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | There is no observable physical damage to the tank and all the contact parts are free from scratches & damages. |  |  |  |
| 2 | Sufficient room for servicing, handling & maintenance is provided (around the machine) |  |  |  |
| 3 | Check the floor space. It should not be inclined. |  |  |  |

Utilities

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | Power Requirement (AC220V/50Hz/Live, Neutral and Earth cable) |  |  |  |
| 2 | Adequate illumination at the Proposed Machine room |  |  |  |
| 3 | Proper Earthing System available |  |  |  |

Equipment compliance

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | Airflow mode (Laminar flow, upward feeding and downward feedback) |  |  |  |
| 2 | Dimension (Outer diameter: W1000*D870*H1700mm, Inner diameter: W800*D800*H1100mm) |  |  |  |
| 3 | MOC: SS304 |  |  |  |
| 4 | Dynamic Pass box name plate present |  |  |  |

Safety compliance

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | All external surfaces are free of sharp edges. |  |  |  |
| 2 | Safety earthling arrangement is available. |  |  |  |

Electrical diagram check

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | Verify the electrical panel wiring diagram |  |  |  |
| 2 | Check whether the position of each component in the electrical is correct |  |  |  |
| 3 | Check whether the wiring of the electrical panel is consistent with electrical diagrams |  |  |  |
| 4 | Check if the electrical diagram is attached to the operation manual |  |  |  |

List of Main Components with their material of construction

| S/N | Component | Origin/ Configuration | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- | --- |
| 1 | Centrifugal Fan | Pass box blower, Impeller: 146mm, Motor power: 0.5HP, Single phase, Voltage: 220/50Hz, Blade material: SS, Airflow: 1000m3/hr. |  |  |  |
| 2 | Liquid tank filter | Model: H14 aluminum alloy, Filtration Efficiency: 99.995% @ 0.3μm |  |  |  |
| 3 | DOP test port | MOC: SS304 |  |  |  |
| 4 | Diffuser | MOC: SS304, Type: Perforated plate diffuser |  |  |  |
| 5 | Return vent | MOC: SS304, Grille type: Perforated grilles |  |  |  |
| 6 | Differential pressure gauge | Manufacturer: Duwei Instruments Ltd., Maximum pressure: 100kPa, D2000-500Pa, P.max, 140oF (60oC) |  |  |  |
| 7 | Ultraviolet germicidal lamp | Model: KC UVC-15W (24), Dimension: 18 inches |  |  |  |
|  | Fluorescent light | Model: KC UVC, Power Rating: 15W, Voltage: 24Vdc, Dimension: 18 inches |  |  |  |
| 8 | Double-layered tempered glass door | MOC: Transparent tempered Glass |  |  |  |
| 9 | HEPA Filter | Class: H14 (99.99% @ 0.3μm), Air velocity: 0.36-0.54m/s, Dimension: 720x670x90mm |  |  |  |
| 10 | Control panel | Model: S1, Input Voltage: AC220V, Frequency: 50Hz, communication method: RS485, Door lock voltage: DC12V |  |  |  |

10.0   INSTALLATION QUALIFICATION REPORT:

Attachment of all reports written as:

#Attachment 1

#Attachement 2 etc.

Date of Installation:

Date of Completion:

11.0 DEVIATION REPORT

Prepare a Deviation report including the justification of acceptance and impact on the function of the system/equipment

DEVAITIONS:

JUSTIFICATION FOR ACCEPTANCE:

IMPACT ON OPERATION:

Written By:										Date:

Reviewed By:										Date:

Approved By:										Date:

12.0 CONCLUSION

13.0 List of Attachment

Attach all completed, signed data record forms

14.0 REPORT APPROVAL

Written By:										Date:

Reviewed By:										Date:

Approved By:										Date: