BIOMEDICAL LIMITED

# INSTALLATION QUALIFICATION (IQ)

# REPORT

# FOR

# WATER FOR INJECTION STORAGE TANK (4000 LITRES)

BIOMEDICAL LIMITED

HORIZONTAL AUTO-PACKING MACHINE INSTALLATION QUALIFICATION PROTOCOL

EQUIPMENT SR. NO. –

EQUIPMENT ID. –

LOCATION – INFUSION WATER TREATMENT PLANT

PROTOCOL No. – BML/PDF/WT/PT/26/001

REPORT No - BML/PDF/WT/RP/26/001

PROVIDED BY:

BIOMEDICAL LIMTED

KWARA STATE, NIGERIA

# TABLE OF CONTENT

Cover Page											1

Table of content										2

Report Format  Approval Sheet								3

Objective											4

Scope											5

Responsibilities and Qualification team							5

Equipment Identification and Description							5

Prerequisite										6

Abbreviations and definitions								6

References											7

Equipment installation Checklist								7-12

Installation Qualification Report								12

Deviation Report										13

Conclusion											14

List of attachments										14

Report Approval										14

- REPORT FORMAT  APPROVAL:

Signatures in this page indicate that this document and its format have been prepared, checked and approved by the personnel concerned. It shall be signed and dated as shown below.

|  | WRITTEN BY: | REVIEWED BY: |
| --- | --- | --- |
| Signature |  |  |
| Position |  |  |
| Date |  |  |

|  | APPROVED BY: | AUTHORISED BY: |
| --- | --- | --- |
| Signature |  |  |
| Position |  |  |
| Date |  |  |

2.0 OBJECTIVE

The purpose of the study is to ensure proper installation of the two WATER FOR INJECTION STORAGE TANK (4000 LITRES) at THE WATER TREATMENT PLANT, INFUSION FACTORY, BIOMEDICAL LIMITED.

This study verifies:

- Qualification of the equipment, reinstallation and to ensure that all background information is performed to assure conformance to BIOMEDICAL LIMITED and manufacturer’s specifications.

- The equipment meets the current good manufacturing practices requirements and all other regulatory obligations.

- No unauthorized or unrecorded modifications have taken place.

- Operation procedures/preventive maintenance procedures have been identified and listed.

- All critical instrumentation has been identified.

- All utilities are properly connected.

- All safety features are accounted for.

- All relevant data have been checked

3.0 SCOPE

- This report is applicable in carrying out the installation qualification of the two waters for injection storage tanks (4000 liters) at the Infusion manufacturing site, Biomedical Limited, Kwara State.

- To be performed after the completion of the design qualification

- To be performed at the time of relocation.

4.0 RESPONSIBILITIES AND QUALIFICATION TEAM

The following departments shall be involved in:

| DEPARTMENT | RESPONSIBILITY |
| --- | --- |
| Engineering Team | Provision of needed utility and machine installation |
| Head Of Engineering | Review of the Installation Qualification Document |
| QA Manager | Final Documentation and system acceptability |
| Superintendent Pharmacist/factory Manager | Authorization |

The following personnel will be involved in the execution of the Qualification

| S/No. | DEPARTMENT | NAME | SIGNATURE |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 3 |  |  |  |
| 4 |  |  |  |
| 5 |  |  |  |

5.0 EQUIPMENT IDENTIFICATION AND DESCRIPTION

IDENTIFICATION

| Equipment Name | WATER FOR INJECTION STORAGE TANK (4000 LITRES) |
| --- | --- |
| Manufacturer’s Name | SAHANI ENGINEERS PVT LIMITED (INDIA) |
| Supplier’s name | VITRA VENTURES (INDIA) |
| Location of Installation | WATER TREATMENT (INFUSION FACTORY) |

DESCRIPTION:

………………………………………………………………………………………………………………………………………………..………………………………………………………………………………………………………………………………………………..

………………………………………………………………………………………………………………………………………………..

………………………………………………………………………………………………………………………………………………..

………………………………………………………………………………………………………………………………………………..

………………………………………………………………………………………………………………………………………………....................................................................................................................................……………..

6.0 PREREQUISITE

The equipment shall confirm the specifications and requirements as specified in the Design Qualification

| S/N | ACCEPTANCE CRITERIA |
| --- | --- |
| 1 | User Requirement specification |
| 2 | Design Qualification |

7.0 ABBREVIATIONS AND DEFINITIONS

| Abbreviation | Definition |
| --- | --- |
| SOP | Standard Operating Procedure |
| MOC | Material of Construction |
| HMI | Human Machine Interface |
| ENGR | Engineering |
| IQ | Installation Qualification |
| QA | Quality Assurance |
| VAC | Voltage Alternating Current |
| S. S | Stainless Steel |
| LTD | Limited |
| °C | Degree Celsius |
| V | Voltage |
| GMP | Good manufacturing practices |
| AC | Alternating Current |
| Amps | Ampere |
| W | Watt |
| SMPS | Switched mode power supply |
| VDC | Voltage Direct Current |
| DC | Direct Current |
| PVC | Polyvinyl Chloride |
| MCB | Miniature Circuit Breaker |
| MCCB | Molded case circuit breaker |
| KW | Kilowatt |
| PLC | Programmable Logic Control |

8.0 REFERENCES:

The list of reference documents, which are referred for preparation and review of this document, is as follows: -

- S.O.P for Installation, Operation & Performance Qualification of equipment & Instrument: BML-QDG-QA-111

- Machine Manual supplied by SAHANI ENGINEERS PVT LIMITED

- Design Qualification supplied by SAHANI ENGINEERS PVT LIMITED

9.0 EQUIPMENT INSTALLATION CHECKLIST:

Pre-Installation Consideration

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | There is no observable physical damage to the tank and all the contact parts are free from scratches & damages. |  |  |  |
| 2 | Sufficient room for servicing, handling & maintenance is provided (around the machine) |  |  |  |
| 3 | Check the floor space. It should not be inclined. |  |  |  |

Assembly of non-assembled items

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | Assemble/connect the tank vent filters, gauges, light bulb, Sensor and ultrasonic sensor |  |  |  |

Utilities

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | Power Requirement (Three-phase, 5 wires, L1, L2, L3, Neutral & Earth 415VAC ±10% 50Hz) |  |  |  |
| 2 | Adequate illumination at the Proposed Machine room |  |  |  |
| 3 | Proper Earthing System available |  |  |  |

Equipment compliance

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | Tank name plate present |  |  |  |
| 2 | Tank Capacity (4000 liters) |  |  |  |
| 3 | Tank MOC: SS316L Contact part, SS304 Non-Contact Part |  |  |  |
| 4 | Tank Serial Number Present (SE86/SE87) |  |  |  |

Safety compliance

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | All external surfaces are free of sharp edges. |  |  |  |
| 2 | Safety earthing arrangements are available. |  |  |  |
| 3 | Emergency Stop Buttons available |  |  |  |
| 4 | Phase indicator is available |  |  |  |

Electrical diagram check

| S/N | Description | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- |
| 1 | Verify the electrical panel wiring diagram |  |  |  |
| 2 | Check whether the position of each component in the electrical circuitry is correct |  |  |  |
| 3 | Check whether the wiring of the electrical panel is consistent with electrical diagrams |  |  |  |
| 4 | Check if the electrical diagram is attached to the operation manual |  |  |  |

List of Main Components with their material of construction

| S/N | Component | Origin/ Configuration | Qualified / Not Qualified | Checked By | Verified By |
| --- | --- | --- | --- | --- | --- |
| MECHANICAL PART LIST |  |  |  |  |  |
| 1 | Tank | SAHANI ENGINEER PVT LTD (Main SHELL DISH: SS316L, JACKET SHELL DISH: SS304, LEGS: SS,304, OUTLET VALVE: SS316L, MAN HOLE: SS316L LIGHT: Screw bulb 220VAC, ELECTRICAL PANEL: SS304 |  |  |  |
| 2 | Sanitary valve | SS316L Flush bottom Valve 2’’ |  |  |  |
| 3 | Air Vent | MATERIAL: S.S316L, TRI CLAMP MOC: S.S304, FILTER: 0.22-micron, Diameter 2’’ LENGTH 5’’, |  |  |  |
| 4 | PUMP | Motor Manufacturer: Hindustram, 415V, 3.7KW/5 H.P, 7.2Amps, 2900RPM, 0.84PF, 50Hz |  |  |  |
| 5 | Pressure Gauge | SHREEJI (MOC: S.S316L, THREADING SIZE: ¼’’ BSP, (0-100Psi/0-7Kg/cm²) |  |  |  |
| 6 | Emergency Button | Manufacturer: TEKNIC, Details: S2 NC Contact, Ratings: A600, IEC947-5-1, EN60947-5-1, 15-240V, 3A |  |  |  |
| 7 | Thermocouple | RADIX (Type: PT 100, Range: -50°C to 250°C, sheath Length: 150mm, sheath Diameter: 6mm, Connection: ½’’ BSP) |  |  |  |
| 8 | Pressure relief Valve | Angle type SS304, Connection Type: ¼’’BSP |  |  |  |
| 9 | SMPS | Manufacturer: Shavison, Model: G41-60-24, INPUT: 230VAC,1.0A, 50/60Hz, OUTPUT: 24VDC, 2.5A |  |  |  |
| 10 | Miniature Circuit Breaker | - Manufacturer: Siemens, Model: 3 POLES, 5SL63167RC, RATINGS: 16Amps - Manufacturer: Siemens, Model: 2 POLES, 5SL62107RC, RATINGS: 10Amps |  |  |  |
| 11 | Control Panel Cooling Fan | Manufacturer: Rexnord, MODEL: EC2-12038 S2 W, RATING: 230VAC, 50/60Hz, 0.05Amps, 4.5W |  |  |  |
| 12 | PLC | - Manufacturer: DELTA, Model: DVP-12SA211R, POWER UNIT: 24VDC, 1.8W, OUTPUT MODULE: 1.5A, 250VAC 50/60Hz Resistive load. 12SA211RW24280812, V3.02A3 - Manufacturer: DELTA DVP-04AD-S2, POWERINPUT:24VDC, 2W, I/O RANGE: -10V--P+10V OR -20mA--+20Ma. 04ad-s20w24270996, v4.18a1 |  |  |  |
| 13 | Human Machine Interface | Manufacturer: Delta Electronics Inc, MODEL: DOP-107BV, Input: 24VDC, CLASS: 2/340Ma (MAX) |  |  |  |
| 14 | Rotary Switch | Manufacturer: TEKNIC, Details: S2 NC Contact, Ratings: A600, IEC947-5-1, EN60947-5-1, 15-240V, 3A |  |  |  |
| 15 | Hooter | Manufacturer: TNI, Model Number: LB22-D24 Ratings: 24VDC, Mounting Diameter 22mm, Compliance: IEC60947-5-1 |  |  |  |
| 16 | Ultrasonic Level Transmitter | Model: ULT-PP-1/ -FP Range: 0- 04Mtr Housing: ABS Plastic Display: LCD Display Power Supply: 24 VDC Output: 420mA (2-wire) Cable Entry:PG11 Diaphragm: PVC Process Connection: G2 (BSP) Protection: IP-66 Process Temp.: -20°C to +80°C Accuracy: ±0.5% Beam Angle: 12.5° Serial No.: 25010028, 25010030 |  |  |  |
| 17 | Contactor | Manufacturer: SIEMES, Model: 3TF31, 240VAC Coil |  |  |  |
| 18 | Thermal overload Relay | Manufacturer: SIEMENS, Rating: 4—6.3Amps |  |  |  |
| 19 | DIN Rail Mounted Fuse Holder | Manufacturer: CONNECTWELL, MODEL: CF4U/CF4UL, 0.2—4mm, 1000v, 6.3Amps |  |  |  |
| 20 | Relay Module, with Relays | Relay module Manufacturer: Agility Relay Manufacturer: Omron, ratings: G5Q-14, Coil voltage: 24VDC, contact rating: 10A at 250VAC or 5A at 30vdc |  |  |  |
| 21 | Temperature Transmitter | Manufacturer: Shavison, input: PT-100, Range: 0-400°C, Output: 0-10VDC, Isolation: 3 Points, Order Code: AS746-311, Auxiliary Supply: 24VDC |  |  |  |
| 22 | Light Indicator | Manufacturer: TNI, Model Number: LP22-A230 Ratings: 230VAC, Mounting Diameter 22mm, Compliance: IEC60947-5-1 |  |  |  |
| 23 | Main Switch (ON/OFF) | Manufacturer: Salzer, Ratings: 16A-S16-61197, 3-POLES |  |  |  |

10.0   INSTALLATION QUALIFICATION REPORT:

Attachment of all reports written as:

#Attachment 1

#Attachement 2 etc.

Date of Installation:

Date of Completion:

11.0 DEVIATION REPORT

Prepare a Deviation report including the justification of acceptance and impact on the function of the system/equipment

DEVAITIONS:

JUSTIFICATION FOR ACCEPTANCE:

IMPACT ON OPERATION:

Written By:										Date:

Reviewed By:										Date:

Approved By:										Date:

12.0 CONCLUSION

13.0 List of Attachment

Attach all completed, signed data record forms

14.0 REPORT APPROVAL

Written By:										Date:

Reviewed By:										Date:

Approved By:										Date: