BIOMEDICAL LIMITED

HVAC VALIDATION PROTOCOL

EQUIPMENT SR. NO. –

EQUIPMENT ID. –

LOCATION – CLEAN ROOM

PROTOCOL No. –  BML/QA/HVAC/PT/001

PROVIDED BY:

BIOMEDICAL LIMTED

KWARA STATE, NIGERIA

Table of Contents

1.0	PROTOCOL FORMAT APPROVAL	3

2.0	OBJECTIVE	4

3.0	SCOPE	4

4.0	RESPONSIBILITIES AND VALIDATION TEAM	4

5.0	EQUIPMENT IDENTIFICATION AND DESCRIPTION	5

6.0	PREREQUISITE:	5

7.0	QUALIFICATION FREQUENCY	6

8.0	QUALIFICATION TESTS	6

AIR VELOCITY, AIR VOLUME, AND AIR CHANGE PER HOUR (ACPH) MEASUREMENTS:	6

INTEGRITY TEST OF HEPA FILTERS	6

DIFFERENTIAL PRESSURE MEASUREMENT	7

TEMPERATURE AND HUMIDITY CONTROL TEST	7

AIRFLOW PATTERN TEST	7

NON-VIABLE PARTICLE COUNT	7

RECOVERY STUDY	8

MICROBIAL MONITORING	8

Passive Air Sampling:	8

Active Air Sampling:	8

9.0	REQUALIFICATION CRITERIA	9

10.0	DEVIATION (IF ANY)	9

11.0	REQUALIFICATION SUMMARY	9

12.0	LIST OF FORM/ANNEXURE/RECORDS	9

13.0	REFERENCE	10

14.0	ABBREVIATION	10

15.0	APPROVAL OF REQUALIFICATION REPORT	10

# PROTOCOL FORMAT APPROVAL

Signatures in this page indicate that this document and its format have been prepared, checked and approved by the personnel concerned. It shall be signed and dated as shown below.

|  | WRITTEN: | REVIEWED: |
| --- | --- | --- |
| Signature: |  |  |
| Position: |  |  |
| Date: |  |  |

|  | APPROVED | AUTHORIZED |
| --- | --- | --- |
| Signature: |  |  |
| Position: |  |  |
| Date: |  |  |

# OBJECTIVE

This protocol aims to provide an outline for the qualification of the HVAC system and to establish documentary evidence to demonstrate that the Air Handling Units (AHUs) are qualified to perform well within the predetermined acceptance criteria of performance as per guideline outlined in this protocol,

# SCOPE

- The scope of this protocol is applicable for the qualification and requalification of the AHUs in Biomedical Limited.

# RESPONSIBILITIES AND VALIDATION TEAM

The following departments shall be involved in:

| DEPARTMENT | RESPONSIBILITIES |
| --- | --- |
| QUALITY ASSURANCE | - Responsible for ensuring the overall qualification of the HVAC - Preparation, review and approval of the protocol and report - To impart training of the team involved in the HVAC qualification - Compile and review reports |
| PRODUCTION | - To provide execution support during the qualification - To review protocol and report |
| QUALITY CONTROL/MICROBIOLOGY | - To review the protocol and report - To perform and provide environmental monitoring reports of the manufacturing area for the microbial load asp per schedule to record all the observations. |
| ENGINEERING | - Reviewing protocol and report - To provide execution and parameter support and ensure proper operation of the system |

VALIDATION TEAM

These personnel shall bear these responsibilities as regards the qualification.

| s/no | Name | Position | Proficiency Status | Signature |
| --- | --- | --- | --- | --- |
| 1 |  | Microbiologist | Trained and qualified |  |
| 2 |  | Chemist | Trained and qualified |  |
| 3 |  | Quality Control Head |  |  |
| 4 |  | Production Supervisor qualified |  |  |
| 5 |  | Engineer-in-charge |  |  |

# EQUIPMENT IDENTIFICATION AND DESCRIPTION

| Equipment Name | HVAC SYSTEM |
| --- | --- |
| Manufacturer’s Name | PHARMINTECH ENGINEERING CO., LTD, CHINA |
| Supplier’s name | PHARMATECH ENGINEERING CO., LTD, CHINA |
| Location of Installation | CLEANROOM |

EQUIPMENT DESCRIPTION/SPECIFICATIONS:

Details of AHUs are

| s/no | AHU no | No of HEPA | No of return riser | capacity | ACPH | Operational temperature and humidity |  | Differential pressure (Pa) |  | Rooms attached |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

# PREREQUISITE:

| S/N | ACCEPTANCE CRITERIA |
| --- | --- |
| 1 | Daily Cleaning |
| 2 | Required materials and instruments are available |
| 3 | Calibration and Preventive Maintenance of Equipment |
| 4 | Gowning procedure of plant personnel for Entry and Exit to the areas. |
| 5 | SOP for operation of FFS |
| 6 | SOP for cleaning of the FFS |
| 7 | Calibration and Preventive Maintenance mechanism |
| 8 | Personnel qualification and hygiene |
| 9 | Training records |
| 10 | Calibration of instruments used for testing eg. Anemometer, particle counter, air sampler etc. |

# QUALIFICATION FREQUENCY

| S/NO | TESTS | REQUALIFICATION FREQUENCY |
| --- | --- | --- |
| 1 | AIR VELOCITY MEASUREMENT AND CALCULATION OF AIR CHANGES | - Once every 6 months - At every filter replacement |
| 2 | Integrity testing of HEPA filter | - Once every 6 months - At every filter replacement |
| 3 | Pressure differential test | - For 3 days (every 6 months), continuous monitoring |
| 4 | Temperature and relative humidity test | - For 3 days (every 6 months), continuous monitoring |
| 5 | Air flow pattern test | - Twice every year |
| 6 | Cleanliness class verification Non-viable particulate count At rest condition and in operation for room classes | - Once in every six months for three consecutive days at define locations - At every filter replacement |
| 7 | Microbial monitoring | - Once in every six months for three consecutive days at define locations. Continuous monitoring in critical/core areas |
| 08 | Recovery test | - Twice in a year |

# QUALIFICATION TESTS

## AIR VELOCITY, AIR VOLUME, AND AIR CHANGE PER HOUR (ACPH) MEASUREMENTS:

- The test shall be performed as per the respective SOP

- Reference SOP and results shall be enclosed with the report.

- The formula to calculate the ACPH is

ACPH=total CFM x 60room volume

- Apparatus required: anemometer, capture hood (calibrated)

- Acceptance criteria: air velocity and ACPH shall be within the design specification. A variation in air volume shall not be ±20% from the design CFM

## INTEGRITY TEST OF HEPA FILTERS

- the test shall be performed as per SOP

- apparatus required:

- acceptance criteria: the leakage rate is NMT 0.01% (ensure zero leakage at joints), upstream concentration should be 100%

## DIFFERENTIAL PRESSURE MEASUREMENT

- measurement shall be performed as per SOP

- calibrated equipment shall be used for measurement

## TEMPERATURE AND HUMIDITY CONTROL TEST

Air handling system shall be in operation for at least 15 minutes prior to performing the activity

In case of manual recording, record the data for 72 hours at an interval of 2 hours frequency

All lights in  the critical and controlled areas should be ON during the testing

Use calibrated thermohygrometerpp

Temperature and RH in the areas shall be checked and recorded in dynamic conditions

- acceptance criteria: shall meet the required specification for monitoring

## AIRFLOW PATTERN TEST

The test shall be performed as per the respective SOP

The test shall be performed at rest and in dynamic conditions.

Video recording of the test shall be made

- apparatus required: fog generator, fog solution, digital video camera

- acceptance criteria: air should flow from high pressure zones to low pressure zones. Air should flow unidirectionally from supply to the return air filter or grill. Videography shall show the room area and name.

## NON-VIABLE PARTICLE COUNT

The test shall be performed as per SOP.

Test shall be performed at rest and in operation

The number of sample locations shall be calculated as shown be below:

| Area of room | Minimum number of sample |
| --- | --- |
| 2 | 1 |
| 4 | 2 |
| 6 | 3 |
| 8 | 4 |
| 10 | 5 |
| 24 | 6 |

- acceptance criteria: the average particle concentration at each of the particle measuring locations should fall below the mentioned class limit.

| Class/grade | At rest |  | In operation |  |
| --- | --- | --- | --- | --- |
|  | 0.5mm | 5.0mm | 0.5mm | 5.0mm |
| A/5 | 3500 | 0 | 3500 | 0 |
| B/6 | 3500 | 0 | 350000 | 2000 |

## RECOVERY STUDY

The test shall be performed as per the SOP

Ensure the required instruments are calibrated.

Recovery study should be performed for Temperature, RH, Differential Pressure

Recording frequency should be two minutes interval

Recovery test for viable counts should be checked on 15 minutes interval.

- apparatus required: magnehelic gauge, hygrometer, thermometer, particle counter.

- Acceptance criteria: the recovery time should not be more than 15 minutes, excluding viable count.

## MICROBIAL MONITORING

To determine the viable particle count test by exposing settle plate and active sampling in the defined areas.

### Passive Air Sampling:

Plates shall be exposed on the predefined locations, and each batch shall be exposed for no less than four hours.

Exposed plates shall be recovered and incubated at the required conditions. Plates shall be observed for microbial growth after 3 and 5 days.

Microbial monitoring shall be done for three consecutive days, once every six months.

- Acceptance criteria:

| Class/grade | Limit (cfu/plate) | Alert limit | Action limit |
| --- | --- | --- | --- |
| A/5 | <1 | <1 | <1 |
| B/6 | 5 | 3 | 4 |
| C/7 | 50 | 30 | 40 |
| D/8 | 100 | 60 | 80 |

### Active Air Sampling:

Fully charged sampler, sterilized sieve, shall be used for every monitoring of the aseptic area.

Active sites of the sampler shall be sanitized properly prior to the exercise with filter 70% IPA before sampling.

Preincubated media plates shall be fitted in the sampler, and its perforated lid placed over the plate. A feed parameter of 1000L of air shall be used for the parameter.

The plate shall be removed carefully, minding not touching the surface of the media and incubated.

Microbial monitoring shall be done for three consecutive days, once every six months.

- Acceptance criteria:

| Area grade | Limit cfu/m3 | Alert limit | Action limit |
| --- | --- | --- | --- |
| A | <1 | <1 | <1 |
| B | 10 | 6 | 8 |
| C | 100 | 60 | 80 |
| D | 200 | 120 | 160 |

# REQUALIFICATION CRITERIA

The system shall be revalidated under the following conditions.

- Periodic requalification - When any major changes or modifications in the system is done - When any major changes are done in the room or module, which will affect the environmental condition of the area. - When major maintenance has taken place in the system which can affect the performance of the AHU

# DEVIATION (IF ANY)

Any deviation observed during the requalification shall be recorded and investigated, with description of deficiency, date observed, person responsible for the corrective action and date assigned duly recorded. The date the corrective action was conducted and completed should be duly recorded as well.

# REQUALIFICATION SUMMARY

The requalification report shall consist of a summary, in narrative form, which shall briefly describe the activity performed along with the observations recorded in relevant exhibit.

The report shall include related documents, references and attachment/annexures which were completed at the time of the revalidation activity

# LIST OF FORM/ANNEXURE/RECORDS

| List of form | List of annexure/records |
| --- | --- |
| Air velocity/airflow measurement and calculation of air changes | Report of air velocity and ACPH |
| Filter integrity test | Report of filter integrity |
| Differential pressure measurement | Report of temperature and RH |
| Temperature and humidity measurement | Report of differential pressure |
| Airflow patter test | Report of non-viable particle count |
| Non-viable particle count test | Environment monitoring report for passive air sampling |
| Recovery | Environment monitoring report for active air sampling |
| Viable particle count – passive air sampling | Report of calibration of anemometer |
| Viable particle count – active air sampling | Calibration report of particle counter |

# REFERENCE

SOP for qualification and requalification of HVAC

# ABBREVIATION

| AHU | Air handling unit |
| --- | --- |
| SOP | Standard operating procedure |
| QA | Quality Assurance |
| CFM | Cubic feet per minute |
| m | Meter |
| HEPA | High Efficiency Particulate Air |
| HVAC | Heating, Ventilation and Air Conditioning |
| ACPH | Air changes per hour |
| DP | Differential pressure |
| RH | Relative humidity |
| REV | Revision |
| No | Number |
| NMT | Not more than |

# APPROVAL OF REQUALIFICATION REPORT

The report shall be recorded, evaluated and shall be approved with the format:

Written By:										Date:

Reviewed By:										Date:

Approved By:										Date: