BIOMEDICAL LIMITED

HVAC VALIDATION REPORT

BML/QA/HVAC/RP/001

| PROTOCOL NUMBER | BML/QA/HVAC/PT/001 |
| --- | --- |
| REPORT NUMBER | BML/QA/HVAC/RP/001 |
| VERSION NUMBER | 00 |
| EFFECTIVE DATE |  |
| REVIEW DATE |  |

ADDRESS:                                               CONTACT DETAILS:

No. 1 Ohimege Road, Industrial Estate,        E-mail:

Ilorin, Kwara State,

Nigeria.

APPROVAL PAGE

|  | WRITTEN: | REVIEWED: |
| --- | --- | --- |
| Signature: |  |  |
| Position: |  |  |
| Date: |  |  |

|  | APPROVED | AUTHORIZED |
| --- | --- | --- |
| Signature: |  |  |
| Position: |  |  |
| Date: |  |  |

TABLE OF CONTENT

| Content |  | Page No. |
| --- | --- | --- |
| HISTORY |  | 4 |
| OBJECTIVE |  | 4 |
| SCOPE |  | 4 |
| VALIDATION TEAM |  | 4 |
| EQUIPMENT DESCRIPTION/SPECIFICATION |  | 5 |
| PROCESS ROOM DESCRIPTION |  | 5 |
| VALIDATION TEST |  | 5 |
|  | AIR CHANGE PERFORMANCE | 5 |
|  | DIFFERENTIAL PRESSURE ACROSS | 8 |
|  | FILTER INTEGRITY | 9 |
|  | PARTICLE COUNTING | 9 |
|  | VIABLE PARTICLE COUNT | 11 |
|  | SYSTEM RECOVERY | 12 |
|  | AIRFLOW PATTERN | 13 |
|  | TEMPERATURE AND RELATIVE HUMIDITY ACROSS | 14 |
| DEVIATION |  | 15 |
| CONCLUSION |  | 16 |
| ENDORSEMENT |  | 16 |
| REFERENCES |  | 17 |
| ABBREVIATION |  | 17 |

HISTORY

| S/NO. | REV. NO. | EFFECTIVE DATE | NATURE OF CHANGE/ REASON FOR REVISION | APPROVED BY QA |
| --- | --- | --- | --- | --- |

OBJECTIVE

This document aims to qualify and certify the performance of the HVAC system with special consideration to the Design of the HVAC and regulating rooms.

SCOPE

- The scope of this protocol is applicable for the qualification and requalification of the AHUs in Biomedical Limited.

| EQUIPMENT NUMBER | MANUFACTURER | LOCATION | BEING VALIDATED |
| --- | --- | --- | --- |
|  |  | INFUSION/SYRUP |  |

VALIDATION TEAM

| s/no | Name | Position | Proficiency Status | Acknowledgement |
| --- | --- | --- | --- | --- |
| 1 |  | Microbiologist | qualified |  |
| 2 |  | Quality Control Head |  |  |
| 3 |  | Production Supervisor |  |  |
| 4 |  | Engineer-in-charge |  |  |

EQUIPMENT DESCRIPTION/SPECIFICATIONS:

Details of AHUs are

| s/no | AHU no | No of HEPA | No of return riser | CFM Capacity | ACPH | Operational temperature and humidity |  | Differential pressure (Pa) |  | Rooms attached |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

PROCESS ROOM DESCRIPTION

| S/No | NAME OF AREA | AREA (SQFT) | HEIGHT (FT) | ROOM VOLUME |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |

VALIDATION TESTS

- AIR CHANGE PERFORMANCE

This test confirms that the air system is balanced and capable of delivering sufficient air volume to maintain minimum air change per hour.

| prerequisite | - Calibration status certificate - Anemometer/air capture hood |
| --- | --- |
| Procedure | - Make sure air stability has been achieved - Segregate the area into corners and it center and take the air velocity - Measure the velocity of the air from each grill/filter in the area - In case of AIR CAPTURE HOOD, the result will be given in CFM/CMH |
| Acceptance criteria | - AHU must maintain and deliver no less than 20 air changes per hour |

| EQUIPMENT CODE |  |  |  |  |  |  |  | EQUIPMENT MAKE |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE |  |  |  |  |  |  |  | AREA CLASS |  |  |  |  |  |  |  |  |  |  |
| PURPOSE |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| INSTRUMENT USED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EQUIPMENT CODE |  |  |  |  |  |  |  |  | MAKE |  |  |  |  |  |  |  |  |  |
| CALIBRATED ON |  |  |  |  |  |  |  |  | RECALIBRATION DATE |  |  |  |  |  |  |  |  |  |
| TEST RESULTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ROOM NAME | DESIGN ACPH | FILTER IDENTITY NUMBER |  | FILTER AREA | VELOCITY READINGS |  |  |  |  |  |  | AVERAGE VELOCITY (V) |  | AIR FLOW CFM |  | TOTAL AIR FLOW CFM | ROOM VOLUME CFT | RESULTANT ACPH |
|  |  |  |  |  | V1 | V2 | V3 |  |  | V4 | V5 |  |  |  |  |  |  |  |
| DATE CONCLUDED |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

- DIFFERENTIAL PRESSURE ACROSS

this test ensures that the air handling unit is designed to maintain sufficient pressure differentials across the room.

| Prerequisite | - Manometer - Calibration status certificate |
| --- | --- |
| Procedure | - Make sure air stability is achieved, and all doors and material transfer apertures are closed. - Restrict entry while performing this test to avoid surge effect - Ensure there are no air bleeds. - Take readings with both the manometer and the magnehelic gauge. |
| Acceptance criteria | 5 to 10 PA between the same class of areas. 10 to 15 PA between different classes of rooms |

| TEST REPORT FOR PRESSURE DIFFERENTIALS ACROSS ROOMS |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE |  |  |  |  |  | TEST FREQUENCY |  |  |  |  |
| ROOM | TIME |  |  | MAGNEHELIC PRESSURE DIFFERENTIAL | HIGH PRESSURE ROOM |  | LOW PRESSURE ROOM | ACTUAL READING |  | REMARK |
| CONCLUSION |  |  |  |  |  |  |  |  |  |  |

- FILTER INTEGRITY

This test aims to confirm if the terminal filter was installed adequately and to ensure there are no air bleeds across the filter gasket.

| Prerequisite |  |
| --- | --- |
| Procedure |  |
| Acceptance criteria | Difference between filter efficiency and percentage leakage must be more than 90%. |

- PARTICLE COUNTING

the test aims to check the correct functioning of the AHU with respect control efficiency and cleanliness against the standard.

| Prerequisite | - Particle counter - Calibration status certificate |
| --- | --- |
| Procedure | - This test shall be carried out at rest and in operation. - The rooms shall be divided into quadrants, and values averaged. - two particle data points shall be measured. - The test shall be conducted for three consecutive days. |
| Acceptance criteria | particle concentration must comply with ISO class for sterile and non-sterile (class 5 and 8 respectively) |

| TEST FOR NON-VIABLE PARTICULATE REPORT |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Instrument used |  |  |  |  |  |  |  |  |
| EQUIPMENT CODE |  |  |  |  | CALIBRATED ON |  |  |  |
| ROOM NAME | DATE/TIME |  | ROOM CONDITION | Average particle count |  |  |  | Remark |
|  |  |  |  | 0.5µm |  | 5.0µm |  |  |
| CONCLUSION |  |  |  |  |  |  |  |  |

- VIABLE PARTICLE COUNT

This test seeks to confirm live microbial cleanliness of an area, and test the efficiency of the AHU to control to regulation.

| Prerequisite | - Air sampler - Calibration status certificate |
| --- | --- |
| Procedure | - Active and passive viable monitoring shall be conducted to monitor the efficiency of AHU |
| Acceptance criteria | viable concentration must comply with ISO class for sterile and non-sterile (class 5 and 8 respectively) |

| Processing Room Grade | Air sample (CFU/m3) | Settle Plates (diameter 90mm) (CFU/4 hours) | Contact Plates (diameter 55mm) (CFU/plates) | Glove print (5 fingers) (CFU/glove) |
| --- | --- | --- | --- | --- |
| ISO class 5 | 10 | 5 | 5 | 5 |
| ISO class 8 | 200 | 100 | 50 | - |

| TEST FOR VIABLE PARTICLE REPORT |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| DATE | ROOM | ACTIVE COUNT |  | GLOVE COUNT |  | PLATE COUNT |  |
| AVERAGE |  |  |  |  |  |  |  |

- SYSTEM RECOVERY

This test checks how much time is required to bring back to normal condition from a worst condition i.e., from peak concentration of particles to normal concentration of particles.

| Prerequisite | - Particle counter - stopwatch |
| --- | --- |
| Procedure | - inject smoke into the room - create the maximum concentration possible using the particle counter. - put on the AHU and run the particle counter continuous without time interval till a stabilized reading is observed that falls within the acceptable limit. - All the while, observed the time it takes to normalize from maximum particulate recorded. |
| Acceptance criteria | System recovery must be less than fifteen minutes. |

| TEST FOR SYSTEM RECOVERY |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ISO CLASSIFICATION |  |  |  |  |  |  | DATE |  |  |  |  |  |
| Instrument used |  |  |  |  |  |  |  |  |  |  |  |  |
| EQUIPMENT CODE |  |  |  | PARTICLE COUNTER |  |  |  | STOPWATCH |  |  |  |  |
|  |  |  |  | Class limit |  |  |  |  |  |  |  |  |
|  |  |  |  | 0.5µm |  |  |  | 5.0µm |  |  |  |  |
| ISO class 5 |  |  |  |  |  |  |  |  |  |  |  |  |
| ISO class 8 |  |  |  |  |  |  |  |  |  |  |  |  |
| TEST RESULTS |  |  |  |  |  |  |  |  |  |  |  |  |
| ROOM NAME | START TIME |  | highest no of particles (0.5µm) |  | Highest no of particles (5µm) | END TIME |  |  | Lowest no of particles (0.5µm) |  | Lowest no of particles (5µm) | Recovery time |
| Deviations: |  |  |  |  |  |  |  |  |  |  |  |  |

- AIR PATTERN FLOW

This test demonstrates that the airflow in a room exhibits a conventional flow, and is not stagnant.

| Prerequisite | - Fog generator - Video camera |
| --- | --- |
| Procedure | - Generate fog near the supply grill. - Record as the smoke moves from the supply grill to the return grill. - Store the video in the cloud and on a CD after adequately labelling the file. - Attach the CD as an annexure to this document. |
| Acceptance criteria | The flow must be towards the return grill, ensuring maximum suction or sweep of the smoke. |

| TEST REPORT FOR AIR PATTERN FLOW |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| INSTRUMENT USED |  |  |  |  |  |
| EQUIPMENT CODE |  | FOG GENERATOR |  | VIDEO RECORDER |  |
| DATE |  |  | FOG CHEMICAL ID |  |  |
| TEST RESULTS |  |  |  |  |  |
| ROOM NAME |  | AIRFLOW DIRECTION AND PATTERN |  | REMARK |  |
| CONCLUSION |  |  |  |  |  |

- TEMPERATURE AND RELATIVE HUMIDITY ACROSS

This test verifies if the AHU is capable of keeping the rooms within its operational temperature and humidity with to heating, cooling and de- humidifying.

| Prerequisite | - Precalibrated Thermos-hygrometer - Stopwatch |
| --- | --- |
| Procedure | - Test to be conducted while room is at rest. - Put on the AHU to the area, and note the time it took to regulate the temperature and humidity to work design conditions. - Take the humidity and temperature at two hours interval. - Repeat the test for two consecutive days, at rest. |
| Acceptance criteria | A uniform temperature and RH is to be maintained across all rooms as per the room’s design. |

| TEST REPORT FOR TEMPERATURE AND RELATIVE HUMIDITY |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| AMBIENT CONDITION |  |  |  |  |  |  |  | LIMIT |  |  |  |  |  |  |  |  |  |
| ACTION LIMIT |  |  |  |  |  |  | ALERT LIMIT |  |  |  |  |  |  |  |  |  |  |
| TIME ON |  |  |  | TIME STABILISED |  |  |  |  |  |  |  |  | TIME ELAPSED |  |  |  |  |
| TEST RESULTS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Location |  | Date | Observed temperature and relative humidity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | T |  | RH | T |  |  | RH | T |  |  |  | RH | T |  | RH |

DEVIATION

CONCLUSION

ENDORSEMENT

| Endorsed by | Name | Signature/Date |
| --- | --- | --- |
| Engineering Manager |  |  |
| Quality Assurance Manager |  |  |
| Factory Manager |  |  |

REFERENCE

SOP for qualification and requalification of HVAC

SOP for operation and control of HVAC

ABBREVIATION

| AHU | Air handling unit |
| --- | --- |
| SOP | Standard operating procedure |
| QA | Quality Assurance |
| CFM | Cubic feet per minute |
| m | Meter |
| HEPA | High Efficiency Particulate Air |
| HVAC | Heating, Ventilation and Air Conditioning |
| ACPH | Air changes per hour |
| DP | Differential pressure |
| RH | Relative humidity |
| REV | Revision |
| No | Number |
| NMT | Not more than |
| RH | Relative humidity |
| T | Temperature |
| V | Velocity |