Water System Validation Report

Approval:

Water System validation Report

|  | WRITTEN: | REVIEWED: |
| --- | --- | --- |
| Signature: |  |  |
| Position: |  |  |
| Date: |  |  |

|  | APPROVED | AUTHORISED |
| --- | --- | --- |
| Signature: |  |  |
| Position: |  |  |
| Date: |  |  |

Test Plan

ANALYSIS REPORT

Table 1.0 Chemical Analysis

Date:

| Sr.No | Sampling Point | Test Conducted | Test Method | Specification | Result | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Raw water | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, colourless, tasteless and odourless |  |  |
|  |  | pH |  | 6.5 – 8.50 |  |  |
|  |  | Conductivity |  | ≤400µ/cm |  |  |
|  |  | Acidity/Alkalinity |  | ≤ 1.5ml of 0.01M NaOH/HCl |  |  |
|  |  | Total Chloride |  | ≤150ppm |  |  |
|  |  | Total Hardness |  | ≤150ppm |  |  |
|  |  | Nitrate |  | ≤0.2ppm |  |  |
|  |  | Heavy Metals |  | ≤0.1ppm |  |  |
|  |  | Sulphate |  | ≤150ppm |  |  |
|  |  | Total Dissolved Solid (TDS) |  | ≤400ppm |  |  |
|  |  | Turbidity |  | ≤ 15NTU |  |  |
| 2. | Post sand filter | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, Colourless, tasteless and odourless |  |  |
|  |  | pH |  | 6.5 – 8.5 |  |  |
|  |  | Conductivity |  | ≤400µ/cm |  |  |
|  |  | Acidity/Alkalinity |  | ≤1.5ml of 0.01M NaOH/≤1.5ml of 0.01M HCL |  |  |
|  |  | Total Chloride |  | ≤150ppm |  |  |
|  |  | Total Hardness |  | ≤100ppm |  |  |
|  |  | Nitrate |  | ≤0.2ppm |  |  |
|  |  | Heavy Metals |  | ≤0.1ppm |  |  |
|  |  | Sulphate |  | ≤150ppm |  |  |
|  |  | Turbidity |  | ≤15NTU |  |  |
|  |  | Total Dissolved Solid (TDS) |  | ≤300ppm |  |  |
| 3 | Post Carbon Filter | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia In- House/ British Pharmacopeia | Clear, Colourless, tasteless and odourless |  |  |
|  |  | pH |  | 6.0 – 8.0 |  |  |
|  |  | Conductivity |  | ≤250µ/cm |  |  |
|  |  | Acidity/Alkalinity |  | ≤1.0ml of 0.01M NaOH/≤1.0ml of 0.01M HCL |  |  |
|  |  | Total Chloride |  | ≤50ppm |  |  |
|  |  | Total Hardness |  | ≤100ppm |  |  |
|  |  | Nitrate |  | ≤0.2ppm |  |  |
|  |  | Heavy Metals |  | ≤0.1ppm |  |  |
|  |  | Sulphate |  | ≤100ppm |  |  |
|  |  | Turbidity |  | ≤5NTU |  |  |
|  |  | Total Dissolved Solid (TDS) |  | ≤100ppm |  |  |

ANALYSIS REPORT

Table 2.0 Chemical Analysis

Date:

| Sr.No | Sampling Point | Test Conducted | Test Method | Specification | Result | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Post Softener Plant | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, colourless, tasteless and odourless |  |  |
|  |  | pH |  | 6.0 – 8.0 |  |  |
|  |  | Conductivity |  | ≤200µ/cm |  |  |
|  |  | Acidity/Alkalinity |  | ≤1.0ml of 0.01M NaOH/≤1.0ml of 0.01M HCL |  |  |
|  |  | Total Chloride |  | ≤50ppm |  |  |
|  |  | Total Hardness |  | ≤100ppm |  |  |
|  |  | Nitrate |  | ≤0.2ppm |  |  |
|  |  | Heavy Metals |  | ≤0.1ppm |  |  |
|  |  | Sulphate |  | ≤150ppm |  |  |
|  |  | Turbidity |  | ≤3NTU |  |  |
|  |  | Total Dissolved Solid (TDS) |  | ≤100ppm |  |  |
| 2. | Post DM Plant | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, colourless, tasteless and odourless |  |  |
|  |  | pH |  | 5.5 – 7.5 |  |  |
|  |  | Conductivity |  | ≤5.1µs/cm at 250C |  |  |
|  |  | Acidity/Alkalinity |  | On addition of bromothymol blue the solution is not blue/ on adittion of methyl red solution the solution is not red |  |  |
|  |  | Total Chloride |  | The appearance of solution should not be changed for at least 15minutes |  |  |
|  |  | Total Hardness |  | A pure blue colour should be produced |  |  |
|  |  | Nitrate |  | ≤0.2ppm |  |  |
|  |  | Ammonium |  | ≤0.2ppm |  |  |
|  |  | Sulphate |  | The solution shows no change in appearance for at least 1 h. |  |  |
|  |  | Heavy Metals |  | ≤0.1ppm |  |  |
|  |  | Total dissolved solid (TDS) |  | ≤0ppm |  |  |
|  |  | Residue on evaporation |  | ≤0.001% |  |  |
|  |  | Oxidizable Substance |  | The test solution remains faintly pink |  |  |

Test Plan

ANALYSIS REPORT

Table 3.0 Chemical Analysis

Date:

| S/No | Sampling Point | Test Conducted | Test Method | Specification | Result | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Post RO | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | pH |  | 5.5 – 7.5 |  |  |
|  |  | Conductivity |  | <5µ/cm |  |  |
|  |  | Acidity/Alkalinity |  | ≤1.0ml of 0.01M NaOH/≤1.5ml of 0.01M HCL |  |  |
|  |  | Total Chloride |  | ≤10ppm |  |  |
|  |  | Total Hardness |  | ≤10ppm |  |  |
|  |  | Nitrate |  | ≤10ppm |  |  |
|  |  | Heavy Metals |  | ≤0.01ppm |  |  |
|  |  | Oxidizable Substance |  | Not detectable |  |  |
|  |  | Ammonium |  | ≤5ppm |  |  |
|  |  | TOC |  | NMT 500 µg/l |  |  |
| 2. | MCDP | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | pH |  | 5.5 – 7.5 |  |  |
|  |  | Conductivity |  | ≤1.3µ/cm |  |  |
|  |  | Acidity/Alkalinity |  | ≤1.0ml of 0.01M NaOH/≤1.5ml of 0.01M HCL |  |  |
|  |  | Total Chloride |  | Not detectable |  |  |
|  |  | Total Hardness |  | ≤0.10ppm |  |  |
|  |  | Nitrate |  | ≤0.1ppm |  |  |
|  |  | Heavy Metals |  | ≤0.01ppm |  |  |
|  |  | Oxidizable Substance |  | Not detectable |  |  |
|  |  | Sulphate |  | Not detectable |  |  |
|  |  | Ammonium |  | ≤1ppm |  |  |
|  |  | TOC |  | NMT 500 µg/l |  |  |

Table 4.0 Test Plan

ANALYSIS REPORT

Chemical Analysis

Date:

| Sr.No | Sampling Point | Test Conducted | Test Method | Specification | Result | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | WFI Storage tank | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | pH |  | 5.5 – 7.5 |  |  |
|  |  | Conductivity |  | ≤1.3µ/cm |  |  |
|  |  | Acidity/Alkalinity |  | ≤1.0ml of 0.01M NaOH/≤1.5ml of 0.01M HCL |  |  |
|  |  | Total Chloride |  | Not detectable |  |  |
|  |  | Total Hardness |  | ≤0.10ppm |  |  |
|  |  | Nitrate |  | ≤1.0ppm |  |  |
|  |  | Heavy Metals |  | ≤0.01ppm |  |  |
|  |  | Oxidizable Substance |  | Not detectable |  |  |
|  |  | Sulphate |  | Not detectable |  |  |
|  |  | Ammonium |  | ≤1ppm |  |  |
|  |  | TOC |  | NMT 500 µg/l |  |  |

Test Plan

ANALYSIS REPORT

Table 5.0 Microbiological Analysis

Date:

| Sr.No | Sampling Point | Test Conducted | Test Method | Specification | Result | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Raw water | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, colourless, tasteless and odourless |  |  |
|  |  | Bacterial count on NA |  | NA - ≤102 cfu/ml |  |  |
|  |  | Fungal count on SDA |  | SDA - ≤102 cfu/ml |  |  |
|  |  | Total viable count |  | - ≤103 cfu/ml |  |  |
|  |  | E.Coli on MA/EMB |  | Nil |  |  |
|  |  | Salmonella Spp on BGA/SSA |  | Nil |  |  |
|  |  | S. aureus on MSA |  | Nil |  |  |
|  |  | Pseudomonas on PSA |  | Nil |  |  |
| 2. | Post sand filter | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | Bacterial count on NA |  | NA - ≤102 cfu/ml |  |  |
|  |  | Fungal count on SDA |  | SDA - ≤102 cfu/ml |  |  |
|  |  | Total viable count |  | - ≤103 cfu/ml |  |  |
|  |  | E.Coli on MA/EMB |  | Nil |  |  |
|  |  | Salmonella Spp on BGA/SSA |  | Nil |  |  |
|  |  | S. aureus on MSA |  | Nil |  |  |
|  |  | Pseudomonas on PSA |  | Nil |  |  |
| 3 | Post Carbon Filter | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | Bacterial count on NA |  | NA - ≤102 cfu/ml |  |  |
|  |  | Fungal count on SDA |  | SDA - ≤102 cfu/ml |  |  |
|  |  | Total viable count |  | - ≤103 cfu/ml |  |  |
|  |  | E.Coli on MA/EMB |  | Nil |  |  |
|  |  | Salmonella Spp on BGA/SSA |  | Nil |  |  |
|  |  | S. aureus on MSA |  | Nil |  |  |
|  |  | Pseudomonas on PSA |  | Nil |  |  |

Test Plan

ANALYSIS REPORT

Table 6.0 Microbiological Analysis

Date:

| Sr.No | Sampling Point | Test Conducted | Test Method | Specification | Result | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Post Softener Plant | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | Bacterial count on NA |  | NA - ≤102 cfu/ml |  |  |
|  |  | Fungal count on SDA |  | SDA - ≤102 cfu/ml |  |  |
|  |  | Total viable count |  | - ≤103 cfu/ml |  |  |
|  |  | E.Coli on MA/EMB |  | Nil |  |  |
|  |  | Salmonella Spp on BGA/SSA |  | Nil |  |  |
|  |  | S. aureus on MSA |  | Nil |  |  |
|  |  | Pseudomonas on PSA |  | Nil |  |  |
| 2. | Post DM Plant | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | Bacterial count on NA |  | NA - ≤102 cfu/ml |  |  |
|  |  | Fungal count on SDA |  | SDA - ≤10 cfu/ml |  |  |
|  |  | Total viable count |  | - ≤102 cfu/ml |  |  |
|  |  | E.Coli on MA/EMB |  | Nil |  |  |
|  |  | Salmonella Spp on BGA/SSA |  | Nil |  |  |
|  |  | S. aureus on MSA |  | Nil |  |  |
|  |  | Pseudomonas on PSA |  | Nil |  |  |

Test Plan

ANALYSIS REPORT

Table 7.0 Microbiological Analysis

Date:

| Sr.No | Sampling Point | Test Conducted | Test Method | Specification | Result | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Post RO | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | Bacterial count on NA |  | NA - ≤102 cfu/ml |  |  |
|  |  | Fungal count on SDA |  | SDA - ≤102 cfu/ml |  |  |
|  |  | Total viable count |  | - ≤102 cfu/ml |  |  |
|  |  | E.Coli on MA/EMB |  | Nil |  |  |
|  |  | Salmonella Spp on BGA/SSA |  | Nil |  |  |
|  |  | S. aureus on MSA |  | Nil |  |  |
|  |  | Pseudomonas on PSA |  | Nil |  |  |
| 2. | Post MCDP | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | Bacterial count on NA |  | NA - ≤102 cfu/ml |  |  |
|  |  | Fungal count on SDA |  | SDA - ≤102 cfu/ml |  |  |
|  |  | Total viable count |  | - ≤102 cfu/ml |  |  |
|  |  | E.Coli on MA/EMB |  | Nil |  |  |
|  |  | Salmonella Spp on BGA/SSA |  | Nil |  |  |
|  |  | S. aureus on MSA |  | Nil |  |  |
|  |  | Pseudomonas on PSA |  | Nil |  |  |

Table 8.0 Test Plan

ANALYSIS REPORT

Microbiological Analysis

Date:

| Sr.No | Sampling Point | Test Conducted | Test Method | Specification | Result | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 2. | WFI Storage Tank | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | Bacterial count on NA |  | Nil |  |  |
|  |  | Fungal count on SDA |  | Nil |  |  |
|  |  | Total viable count |  | Nil |  |  |
|  |  | E.Coli on MA/EMB |  | Nil |  |  |
|  |  | Salmonella Spp on BGA/SSA |  | Nil |  |  |
|  |  | S. aureus on MSA |  | Nil |  |  |
|  |  | Pseudomonas on PSA |  | Nil |  |  |

Table 9.0 Test Plan

ANALYIS REPORT

Microbiological Analysis

Date:

| Sr.No | Sampling Point | Test Conducted | Test Method | Specification | Result | Remark |
| --- | --- | --- | --- | --- | --- | --- |
| 1. | Mixing Tank | Physical Test: Colour, taste and odour | In- House/ British Pharmacopeia | Clear, tasteless and odourless |  |  |
|  |  | Bacterial count on NA |  | Nil |  |  |
|  |  | Fungal count on SDA |  | NIL |  |  |
|  |  | Total viable count |  | Nil |  |  |
|  |  | E.Coli on MA/EMB |  | Nil |  |  |
|  |  | Salmonella Spp on BGA/SSA |  | Nil |  |  |
|  |  | S. aureus on MSA |  | Nil |  |  |
|  |  | Pseudomonas on PSA |  | Nil |  |  |

Results/ Data Analysis

All analytical results must meet the specified limits and annual water quality review will be use to set the minimum acceptance criteria.

________________		____________________

Chemical Analyst 		Microbiologist

Sign/ Date		Sign/Date

__________________		_____________________

Q.A. Manager		Superintendent Pharmacist

Sign/Date		Sign/Date