- OBJECTIVE:

To describe the procedure to monitor the microbial load of the environment and to ensure control over viable count of the clean area in the manufacturing unit of Biomedical Ltd. Subsidization

- SCOPE:

This SOP applies to the monitoring of the microbial load of the clean area in the manufacturing unit in Biomedical Limited.

3.0 RESPONSIBILITY/ACCOUNTABILITY:

- Microbiologists are responsible for following this SOP

- The Quality Control Head is to ensure the procedure outlined is followed.

- ABBREVIATIONS AND DEFINITIONS

- TSA: Tryptone Soya Agar

- SDA: Sabouraud Dextrose Agar

- CFU: Colony forming unit

- IPA – Isopropyl Alcohol

- PROCEDURE

- Sterilize the petri dishes in autoclave at 1210c for 15- 20minutes

- Prepare the TSA and SDA media required for plate exposure as per sop for media preparation BML-QDG-MC-001

- The work bench and the Laminar Flow Cabinet should be disinfected with 70% IPA

- Pour about 15ml to 20ml of sterilized media cooled to 450c aseptically into different sterile Petri-dishes under LAF and allowed to solidify or set.

- After solidification, pre incubate all the media containing petri dishes for 24 hours in an inverted position for detecting any contamination during plate pouring operations

- After incubation, examine all the petri plates without contamination for plate exposure operation

- Plates should be labeled accordingly

- Sanitize the sampling box with 70%IPA

- Place all pre incubated media containing plates in the sampling box to areas for exposure

- Expose the petri plates at each location following the environmental bioburden surveillance location list for clean area BML-QDG-MC-010-L01 by removing the upper lid of the petri plate and placing the media containing part at a point. Expose the petri plates for 4 hours

- After completion of 4 hours of exposure, close the petri plate with lid, collect all the petri plates in same sampling box and carry all exposed plates to laboratory

- Incubate all exposed petri plates in incubators at 20-25oc for 72 hours for SDA plates and 30-35oc for 48 hours for TSA plates in inverted position

- After incubation, count the number of colony forming units (cfu) per plate and fill in the environmental monitoring record sheet for infusion clean area BML-QDG-MC-010-F01 respectively.

- Dispose contaminated plates (if any) according to SOP for microbial waste disposal

BML-QDG-MC-008

Reporting

Fumigation exercise should be done if the Microbial level of the area is confirmed high or above the stated limit.

- WHO limit ------NMT 200 cfu

- Alert limit ------- NMT 50 cfu

- Action limit ------NMT 100 cfu

Materials and Equipment

- Sterile Petri plates

- Sterile Tryptic Soyabean Agar, Sabouraud dextrose agar.

- 70% IPA

- Sterile Cotton Wool

- Laminar Flow Cabinet

- Incubator

- Sampling box

- autoclave

Safety, Health and Environment Precautions

  - Wear appropriate PPE

- REFERENCE/ENCLOSURE

- Environmental monitoring record sheet for infusion clean area - BML-QDG-MC-010-F01

- Environmental monitoring record sheet for syrup clean area - BML-QDG-MC-010-F02

- Environmental bioburden surveillance location list for clean area - BML-QDG-MC-010-L01

- TRAINING INVOLVEMENT

Quality Control Head

Microbiologist

8.0 DISTRIBUTION AND CONTROL:

| MASTER COPIES | QUALITY ASSURANCE |
| --- | --- |
| CONTROLLED COPIES | MICROBIOLOGY LABORATORY |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 02 | ### 01 | To Update |
| ### 03 | ### 02 | - Inclusion of enclosures format - Change in sop format generally |