- OBJECTIVE:

The purpose of this SOP is to provide a consistent procedure for monitoring and maintaining the appropriate air differential between a cleanroom and its adjacent areas.

- SCOPE:

This SOP applies to all cleanrooms and associated areas within the facility that require pressure differentials for contamination control, such as buffer areas and surrounding environments.

- RESPONSIBILITIES/ACCOUNTABILITIES:

•	QA Personnel: Ensure that daily monitoring is performed and record the data accurately.

•	Engineering Department: Respond to any deviations and take corrective actions.

•	Quality Control/Assurance: Review monitoring records and ensure compliance with established standards.

- ABBREVIATION AND DEFINITIONS

- HVAC - Heating Ventilation Air Conditioning

- Pa- pascal

- PROCEDURES

- Verify the differential pressure gauge is calibrated and in good working condition.

- Confirm the cleanroom and adjacent areas are operating according to their design parameters.

- Take readings of the differential pressure between the cleanroom and adjacent areas.

- Perform the monitoring task at the established frequency, typically twice a day (morning and afternoon).

- Record the measured differential pressure value in the designated logbook.

- Note the date, time, and personnel performing the task.

- A positive pressure differential of at least 5-20 Pa between cleaner and less clean rooms is generally required.

- Specific requirements may vary based on the ISO class and the nature of the process.

- If the measured pressure is outside the acceptable range, immediately inform the Engineering Department.

- Engineering personnel should investigate the cause and implement corrective actions.

- Quality Assurance reviews the recorded data to ensure continuous compliance.

- All personnel responsible for monitoring must be trained on the proper use of the differential pressure gauge, understanding of the acceptance criteria, and the correct procedure for reporting deviations.

- Materials, Equipment, Apparatus and Reagents

- Differential Pressure Gauge/Sensor: A calibrated instrument to measure the pressure difference.

- Logbook/Data Sheet: For recording monitoring results.

- REFERENCE AND ENCLOSURE

Who guidelines

- TRAINING INVOLVEMENT

| All departmental managers | All sectional heads |
| --- | --- |
| QA Doc. Unit staff | All staff |

- DISTRIBUTION AND CONTROL:

| MASTER COPIES | QUALITY ASSURANCE |
| --- | --- |
| CONTROLLED COPIES | ALL DEPARTMENT |

9.0 CHANGE HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| 00 | Nil | First issue |
| 06 | 05 | - Change in sop format. - Inclusion of traceability of enclosures to parent SOP |

Annexure I

PRESSURE DIFFERENTIAL MONITORING LOG RECORD

Doc. No: BML/QA/PRE/001

Form No.: PRE001

SOP Ref. No; BML/QA/017

DEPARTMENT:                                                                                                UNITS:

EQUIPMENT I.D NO.:                                                                                      LIMIT:

| Date | Time | Pressure differential ( mm of water) | Observed by | Verified by | Remarks ( if any) |
| --- | --- | --- | --- | --- | --- |