- Objective: To ensure fume hoods provide adequate containment for hazardous materials, protecting lab personnel and preventing contamination, as required by Good Laboratory Practices (GLP).

- Scope : this SOP applies to all fume hoods used in the Chemical Laboratory in Biomedical Ltd, Ilorin. Kwara State.

- Responsibilities

Quality Control Analyst/Laboratory Assistant: Perform daily pre-use checks, follow correct operating procedures, and report issues.

Technical Officer: Conduct professional, scheduled calibration and maintenance.

Equipment:  -	Calibrated thermal anemometer, tape, measuring tape.

- ABBREVIATION AND DEFINITIONS

FT- Feet

e.g - example

- Procedure

- Conduct a visual inspection by checking the sash, seals, and glass for damage.

- Verify lights, alarm system, and digital airflow display (if present) is working.

- Use a tissue strip at the sash opening (set to working height, e.g., 18 inches) to confirm airflow; it should be pulled inward.

- Ensure the digital monitor if present shows a reading within the safe zone.

- Calibration of the equipment must be done by the Senior Analyst/ Technical Officer

- Ensure the hood is clean and free of obstructions before use.

- Keep the sash as low as possible (working height) during use.

- Divide the opening into a grid (e.g., 1ft x 1ft squares).

- Measure face velocity at the center of each grid square using the anemometer on a stand.

- Record all readings and calculate the average face velocity

- Maintain calibration records, including dates, readings, and technician details.

Frequency: periodically as per schedule, using calibrated equipment.

Precautions

- Keep fume hood alarms or monitors on

- Avoid putting one’s head in the fume hood

- Do not use fume hood as permanent storage for chemicals or equipment

- Cap or cover chemical containers when they are not being used

- Properly label chemical containers

- REFERENCE AND ENCLOSURE

- ENCLOSURE 1- Calibration Record of Fume Cupboard- BML-QDG-QA-050-FO1

7.0 TRAINING INVOLVEMENT

| Quality Control Manager | Quality Control Analyst |
| --- | --- |
| QA Doc. Unit staff | Laboratory Assistant |

8.0 DISTRIBUTION AND CONTROL:

| MASTER COPIES | QUALITY ASSURANCE |
| --- | --- |
| CONTROLLED COPIES | ALL DEPARTMENT |

9.0 CHANGE HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| 00 | Nil | First issue |
| 06 | 05 | - Change in sop format. - Inclusion of traceability of enclosures to parent SOP |

Enclosure 1

Calibration record of Fume Cupboard

Sop Ref.No.: BML/QDG/QA/050

Doc .No: BML/ QDG/QA/050/F01