- OBJECTIVE:

To run the RO Plant without breakdown, to increase the life of the membrane and to reduce the excesses mechanical pressure on the membrane provide the instructions for Operating the Reverse Osmosis Machine.

- SCOPE:

To provide written guidelines for daily Operating the Reverse Osmosis Machine

- RESPONSIBILITY/ACCOUNTABILITY:

WTP Officer, Quality Assurance Officer, Chemist, Technical Officers, Q.A Manager, Supt. Pharmacist

- ABBREVIATIONS AND DEFINITIONS:

TDS – Total dissolve solid

RO – Reverse Osmosis Machine

- PROCEDURE:

START UP RO

- Check the main power supply is correct and 3 Phase is coming properly.

- Ensure there is enough water in the storage tank that supplies the RO system.

- Ensure that the outlet valve from RO is open.

- Ensure the reject valve is completely open

- Turn-on the main switch

- Start the feed water pump and allow to expel air from the line and micron filters.

- Start the permeate water pump and adjust the feed water valve gradually to stabilize the flow rate.

- Gradually increase the flow rate by reducing the feed water gate valve (reject valve).

- Ensure the four stages of pressure gauge should not exceed 1.5Mpa.

- Check the normal parameter of RO like: Appearance, Clarity, Odour, Ph, TDS, and conductivity and record in a book.

SHUTTING DOWN

- Turn –off the permeate water pump.

- Turn – off the feed pump.

- Turn – off the main switch.

PRECAUTIONS

- The pressure on the membrane should not be more than 1.5MPa ( 220PSI)

LIST OF REPLACEABLE MATERIALS

- Micron filter Cartridge

- Membranes

FREQUENCY OF REPLACEMENT

Cartridge - 2 weeks

Membrane- This is dependent on the operational condition. Replacement of membranes should be done when it has processed 30,000,000 litres of water or 6months after installation, whichever comes first.

- REFERENCE/ENCLOSURE:

Inhouse

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |