- OBJECTIVE:

This SOP established the procedures for operation of Multi Column Distillation Plant.

- SCOPE:

This SOP involves the effective utilization of Multi Column Distillation Plant

- RESPONSIBILITY/ACCOUNTABILITY:

Water treatment officer, Q.A. Officer, Q.A. Manager. SP/FM

- ABBREVIATIONS AND DEFINITIONS:

PPE- Personal Protective Equipment

SOP – Standard Operating Procedure

PLC- Programmable Logic Machine

HMI – Human Machine Interface

- PROCEDURE:

START UP PROCESS

Ensure there is enough water in the feed water tank for M.C.D.P.

- Switch on the control panel from the main supply

- Open the steam supply valve slowly till steam rises to 5Bar on the steam pressure gauge

- Ensure there is supply of compressed air of about 6Baron the pressure gauge

- Input the operation password and click on the PLC (Programmable Logic Controller) display to start the plant

- Feed pump starts automatically after 3minutes

- Cooling pump will come on when distilled water temperature attains 70°C

- Regulate PRV and steam valve to maintain pressure at 134°C on the controller otherwise the low steam alarm buffers on the PLC display

- Ensure the distilled water temperature is maintained and not above 80C

- To stop caution alarm sound, press F3 button on the PLC display and adjust according to the PLC instruction

- Distilled water is generated when PLC display shows process ok on the visual screen

SHUTDOWN PROCESS

- Close the steam supply valve

- Message display on HMI “SHUT”

- Boiler steam valve OFF ( in case of manual need to open manually as per function requirement)

- Feed water will start up to first column level switch input come then feed pump will off. If due to pump will OFF after fix time (2min-fix)

- Cooling pump will start up to cooling pump cut-off point temperature set point. When cooling water temperature achieve less than cooling pump cut-off temperature set valve, then cooling pump go off. At this time, last column purging valve, venting valve, and dumping valve remains ON

- Now all valves will go off after completion of shutdown timer

NOTE

- When Shutdown cycle is running don’t take any action until the process is complete

- Open manually all the column condensate drain valves to discharge any water remaining in the columns and close back after sometime.

- Switch OFF the main supply.

MANUAL

- Close the Boiler steam valve

- Stop the feed pump after steam pressure is lower than set pressure

- After reducing distill water temperature low set point, stop the cooling pump

- Open the column condensate drain valve and close back the drain back afterwards

- Open all manually operated valves

- SHUTDOWN the main supply.

NORMAL DAILY OPERATION

- Check the direction of both pumps

- Drain out manually all columns through the valve

- Check periodically the steam trap, service it if required.

FREQUENCY: Daily

- REFERENCE/ENCLOSURE:

In-house

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |