- OBJECTIVE:

To run the DM Plant continuously unless the plant is exhaust. To regenerate the De-ionizer again with the recommended quantity of acid and alkali, by giving a sufficient contact time, and by rinsing the exchanger with water properly.

- SCOPE:

This SOP involves the effective operation and regeneration of DM.

- RESPONSIBILITY/ACCOUNTABILITY:

Water treatment Officer, Q.C Chemist, Q.A Manager, Sup. Pharmacist/Factory Manager

- ABBREVIATIONS AND DEFINITIONS:

HCL- Hydrochloric

NaOH- Sodium Hydroxide

DM- Di-mineralized

- PROCEDURE:

- Ensure that valve (V3, V6, V7, V8 and V9) are in lock position.

- Also ensure that valve (V1, V2, V4, and V5) are in open position

- Regeneration of both modules can be done simultaneously

Module:

REGENERATION OF: CATION EXCHANGER

-  Backwash the Cation Exchanger module for 10minutes.

-  Switch the multiport valve to brine and slow suction mode.

CIRCULATION OF HCl

- Fill 60litres of water into the chemical tank and add 6litres of Hydrochloric Acid (Hcl).

- Dip the suction pipe into the solution of Hcl and water and stir homogeneously

- Start the feed pump and allow the solution of Hcl and water to suck into the module.

- When the solution is consumed, stop the feed pump and give 30minutes of contact time.

RINSING

- Switch the multiport valve to fast rinse and start the feed pump for rinsing process.

- Check the pH, conductivity and hardness value of the rinse water respectively.

- Stop the feed pump when : pH is within the range of 6.0-7.5, conductivity 1-5µ, hardness 0 ppm.

- Set the multi-port valve to service mode for use

REGENERATION OF: ANION EXCHANGER

-  Backwash the Anion Exchanger module for 10minutes.

-  Switch the multiport valve to brine and slow suction mode.

CIRCULATION OF NaOH

-  Fill 60litres of water into the chemical tank and add 4kg of Sodium Hydroxide (NaOH).

- Dip the suction pipe into the solution of NaOH and water and stir homogeneously

- Start the feed pump and allow the solution of NaOH and water to suck into the module.

- When the solution is consumed, stop the feed pump and give 30minutes of contact time.

RINSING

- Switch the multiport valve to fast rinse and start the feed pump for rinsing process.

- Check the pH, conductivity and hardness value of the rinse water respectively.

- Stop the feed pump when : pH is within the range of 6.0-7.5, conductivity 1-5µ/cm, hardness 0 ppm.

- After the regeneration, suction and rinsing  process is completed, adjust the multi-port

valve to service mode.

- Lock valve (V1, V4, V7, V9)

- Open valve (V2, V3, V5, V6, V8)

- Start the feed pump and flush for 5 minutes

- Check the pH, conductivity and hardness value ensuring it conforms with the standard specifications respectively. (pH is within the range of 6.0-7.5, conductivity 1-5µ/cm, hardness 0 ppm)

- Ensure valve V8 is closed and valve V9 is opened and start processing purified Di-mineralized water

PREVENTIVE MAINTENANCE OF DM PLANT

Daily:

- Ensure the online ph and conductivity are working properly.

- Check enough water in raw water storage tank

- Check, multiport valve is working very well and it is in proper position.

- Check the feed pump is working properly and sucking acid or alkali properly. Test suction system with water.

- Check the sunction hose for leakages

- Check the pressure gauge OK.

PRECAUTIONS IN HANDLING OF HAZARDOUS CHEMICALS:

- Make proper system of handling of hazardous chemicals like: Hydrochloric acid, Sodium hydroxide or any other chemicals used in this process.

- Use PPE (Personal Protective Equipment) while handling these chemicals.

- Insure, the chemicals are not exposed in open air.

- Give proper training to the concerned people in handling of chemicals & process when the deputed persons (operator, chemist, engineer) are either new or semi-skilled or doesn't know about it.

- Display one chart near DM plant describing: 1. Precautions in Handling of chemicals 2. Important phone number in case of accidents like: ambulance, Safety officer of the factory, police control room, nearest hospital emergency number, General Manager, Quality control manager etc.

- Note each incident, accident in the log book and analyze the cause of incident/accident.

- In case of accident, immediate inform to HOD and concern to a medical doctor immediately.

FREQUENCY: This is dependent on the operational condition. Regeneration is carried out when the plant has processed 18000 liters of water at the duration of 6hours or when the conductivity and pH of DE-IONISED water is not within specification i.e conductivity range (0 – 5.0µ/cm) and pH range (5.0 – 7.5).

- REFERENCE/ENCLOSURE:

In-house

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |