- OBJECTIVE:

To run the Softener Plant continuously unless the plant is exhaust. To regenerate the Softener with the recommended quantity of (Sodium chloride) Nacl, by giving a sufficient contact time, and by rinsing the exchanger.

- SCOPE:

This SOP involves the effective operation and regeneration of Softener Plant.

- RESPONSIBILITY/ACCOUNTABILITY:

Water treatment Officer, Q.C Chemist, Q.A Manager, Sup. Pharmacist/Factory Manager

- ABBREVIATIONS AND DEFINITIONS:

Sodium Chloride - NaCl

- PROCEDURE:

REGENERATION OF SOFTENER

-  Backwash the softener module for 10minutes.

-  Switch the multiport valve to brine and slow suction mode.

-  Fill 60litres of water into the chemical tank and add 6kg of sodium chloride (Nacl).

- Dip the suction pipe into the salt and water solution.

CIRCULATION OF Nacl

- Start the feed pump and allow sucking the Nacl solution into the module.

- When Nacl is consumed, stop the feed pump and give 30minutes of contact time.

RINSING

- Switch the multiport valve to fast rinse and start the feed pump for rinsing process.

- Check the pH, conductivity and hardness value of the rinse water respectively.

- Stop the feed pump when: pH is within the range of 6.0-7.5, conductivity 50- 100, hardness 50-20 ppm.

Frequency: After Every 24hrs or 48hrs or when the plant is exhausted.

Module: Softener plant.

- REFERENCE/ENCLOSURE:

In-house

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |