- OBJECTIVE:

To provide the method of De- scaling multi column distillation plant.

- SCOPE:

This SOP involves effective utilization of the Multi Column Distillation Plant.

- RESPONSIBILITY/ACCOUNTABILITY:

Water treatment Operator/Officer, Engineer, Q.C Chemist.

- ABBREVIATIONS AND DEFINITIONS:

SOP- Standard Operating Procedure

PLC- Programmable Logic Control

HMI- Human Machine Interface

- PROCEDURE:

START UP PROCESS

- Turn on the MCDP main switch.

- Open each columns drain valve completely to drain any water left in the column.

- Open the steam inlet valve and ensure the pressure is at least 0.3mpa on the pressure gauge.

- Ensure there is supply of compressed air and ensure is at least 0.5mpa.

- Open the steam by-pass line to allow free initial circulation of steam.

- Click on automatic mode for the plant to start.

- Plant will start automatically when industrial steam is 5.0% and the target pressure is +0.3mpa.

- Monitor the temperature of each column on the PLC screen, when the temperature of the first              column.

- Effect rises above 100 degrees, close each of the columns drain valve.

- Close the steam by-pass line.

- The inlet valve to WFI will open and turn green on the PLC screen when the plant conforms to    all the required specifications and WFI will be generated.

SHUTDOWN PROCESS

- Close the steam supply valve.

-  Click on Automatic shutdown on the PLC screen.

- The temperature of the inlet steam and each of the columns will go down gradually.

- Open each of the columns drain valve to drain out the water in each column.

- REFERENCE/ENCLOSURE:

In-house

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |