- OBJECTIVE:

To replace the DM & Softener plant resins used for ion exchange in the demineralized plant and softener plant.

- SCOPE:

This SOP covers the procedure for emptying and replacing of DM and Softener plant resins.

- RESPONSIBILITY/ACCOUNTABILITY:

- Water treatment Operator/Officer, Engineer, Q.C Chemist.

- It is the responsibility of Biomedical Limited to provide PPE for its qualified employee

- It is the responsibility of contractors to provide PPE for their qualified staff

- ABBREVIATIONS AND DEFINITIONS:

DM Plant- De-mineralized plant

PPE- Personal Protective Equipment

SOP- Standard Operating Procedure

- PROCEDURE:

- Emptying and replacement process:

- Disconnect the multiport valve at the top of the RF column

- Ensure the top of the column is open for proper discharging of the resins and remove the pipe inside the RF column

- Discharge the resins inside the column completely and rinse the column thoroughly with DM water

- Return the removed pipe back into the column

- Ensure that the pipe is properly installed (well centralized in the column

- Ensure that the top of the pipe is covered to prevent the resins from trapping inside it.

- Add 20 liters of water to the column and fill it with : For : cation exchanger (7 bags),  anion exchanger (6 bags) and softener plant (7 bags of cation resins)

- Return the multiport valve to the top of the column and tighten properly

- Backwash the plant thoroughly to decolorize the newly installed resins

- Regenerate the cation and the anion plant with 15liters of Hydrochloric acid and 15 Kg of sodium hydroxide respectively, and also regenerate softener plant with 15kg of sodium chloride (NaCl)

- Allow contact time of about 30 minutes before rinsing

- After rinsing, set the multiport valve to service mode and check the quality of the water as per SOP standard

- Take a sample of newly processed water and ensure it conforms to the specifications on the checklist e.g. Conductivity, pH, Hardness e.t.c.

- Give sample of water to QC for analysis

Frequency:

This is dependent on the operational condition. Replacement of resins should be done when it has processed 60,880,000 litres of water or 12 months after installation, whichever comes first.

- REFERENCE/ENCLOSURE:

In-house

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |