- OBJECTIVE:

To provide a method of replacing sand and carbon filters.

- SCOPE:

This SOP covers the procedure for replacing sand and carbon filters.

3.0 RESPONSIBILITY/ACCOUNTABILITY:

Water treatment Operator/Officer, Engineer, Q.C Chemist, Microbiologist.

- ABBREVIATIONS AND DEFINITIONS:

PPE- Personal Protective Equipment

SOP- Standard Operating Procedure

- PROCEDURE:

Emptying and replacement process:

- Drain all the water in the columns

- Loose the bolt and nuts from the top and side completely to allow easy access when discharging the components inside

- Discharge the sand and carbon completely and flush the inner part of the column with water

- Fill in 8 bags of sand in the column starting with gravel at the base, coarse in the middle and fine sand at the top respectively.

- Fill in 8 bags of activated carbon in the column

- Fix back the bolt and nut and ensure its well tightened

- Backwash the plant thoroughly to decolorize the newly install sand and carbon filters and also remove dirt

- After rinsing, set the multiport valve to service mode and check the quality of the water as per SOP standard

- Take a sample of newly processed water and ensure it conforms to the specifications on the checklist e.g. Conductivity, pH, Hardness etc.

- Give sample of water to QC for analysis

Frequency:

- This is dependent on the operational condition. Replacement of  sand and carbon filters

Should be done when it has processed 63,880,000 litres of water or 12 months after installation, or whichever comes first.

REFERENCE/ENCLOSURE:

In-house

- TRAINING INVOLVEMENT

| Chief Engineer | Engineer-Incharge, Operators/Assistants. |
| --- | --- |

8.0 DISTRIBUTION AND DOCUMENTATION CONTROL:

| MASTER COPIES | DOCUMENTATION UNIT |
| --- | --- |
| CONTROLLED COPIES | WATER TREATMENT UNIT |

9.0 REVISION HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| ### 00 | ### Nil | First issue |
| ### 06 | ### 05 | - Inclusion of enclosures format - Change in sop format generally |