- OBJECTIVE

To lay down an approved procedure for cleaning and operation of the dispensing booths.

- SCOPE

The following procedures are adopted for the cleaning and operation of the dispensing booths located in the weighing rooms of the Production.

- RESPONSIBILITY/ACCOUNTABILITIES

- The Production Supervisor ensures the proper implementation of the cleaning and operation procedure carried out by the process operators.

- IPQA and production pharmacist ensure the implementation of the procedure and its effectiveness.

- ABBREVIATION AND DEFINITIONS

HEPA Filter: High Efficient Particle Air Filter.

5. PROCEDURE

CLEANING PROCEDURE

FOR CLEANING AT THE BEGINNING OF A SHIFT AND DURING PRODUCT CHANGE OVER.

- Switch off the main power source for the equipment

- Clean the external surface of the dispensing booth.

- Mop the external surfaces with clean, dry, lint free cloth damped with potable water

- Finally wipe with clean, dry, lint free cloth dampened with 70% ethanol and allow it to dry.

- Call the Engineers to clean the primary and secondary filters if change of product is required.

- Fill the cleaning log form BML/PDS/PR/013/F01 of the dispensing booth.

- Attach the ‘CLEANED’ equipment status label on the equipment.

- Call Quality Assurance personnel for inspection and clearance

- Ensure QA approval before commencing the next operation.

FOR WEEKLY CLEANING

- Switch off the main power source for the equipment.

- Ensure the previous dispensed material containers, devices like scoops, spatula are removed from the sampling/dispensing area.

- Remove the powder from floor and outer surface of the dispensing booth pre filter frame, return riser filter, and side panel.

- Mop the entire surface of the pre filter frame, return riser filter and side panel with clean dry lint free cloth with potable water.

- Finally wipe with clean dry lint free cloth damped with 70% Ethanol solution and allow it to dry.

- The dispensing booth is to be cleaned at the time of every product change over.

- Record this operation in the cleaning log form BML/PDS/PR/013/F01

- Attach ‘CLEANED’ equipment status label on the equipment.

OPERATIONAL PROCEDURE

- Ensure the Zero reading in the Magnehelic gauge of dispensing unit, while the dispensing booth is off.

- Ensure the equipment is in clean state.

- Switch ON the main power supply.

- Switch on the light and start the blower.

- Allow the dispensing booth run for at least 15 minutes before use.

- Always open material for dispensing when system is ON.

- Close the poly bag/containers of sampled/dispensed material under dispensing booth before taking it out.

- Switch-off equipment after use.

- Fill the dispensing booth usage log form BML/PDS/PR/013/F02 for the process done.

6. REFERENCES/ENCLOSURE

- Operation and Instruction manual for Dispensing booth Machine.

- Dispensing booth cleaning log form - BML/PDS/PR/013/F01

- Dispensing booth usage log form - BML/PDS/PR/013/F02

7. TRAINING INVOLVEMENT

| Production operator | All sectional heads |
| --- | --- |
| IPQC |  |

8. DISTRIBUTION AND CONTROL

| MASTER COPIES | QUALITY ASSURANCE |
| --- | --- |
| CONTROLLED COPIES | PRODUCTION |

9. CHANGE HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| 00 | Nil | First issue |
| 06 | 05 | - Change in sop format. - Inclusion enclosures to parent SOP |