- OBJECTIVE:

To describe the procedure to be followed in the fumigation of the production environment and the factory to achieve considerable reduction of bio-burden and ensure conformity to required specification.

- SCOPE:

This SOP covers the fumigation process to be carried out in all the production environment and the factory.

- RESPONSIBILITIES/ACCOUNTABILITIES:

- Laboratory Assistant or Technician of the production department shall be responsible for the fumigation of the area as per instructions written in this SOP.

- Production supervisor or IPQA officer shall be responsible for fumigation of the production area as per instructions are written in this SOP.

- Engineering Operator or Technician shall be responsible for the start and stop of AHU’s of the area under fumigation as per instructions written in this SOP.

- Head of the department/ designee of respective areas, Engineering and QA shall be responsible for compliance of this SOP.

- ABBREVIATION AND DEFINITIONS

- AHU : Air Handling Unit

- NA: not applicable

- QA: Quality Assurance

- SOP: Standard Operating Procedure

- CCR: Change Control Record

- PROCEDURES

PRECAUTIONS

- Wear hand gloves, goggles and nose masks during the preparation and fumigation exercise.

- No manufacturing/ packaging activity shall be carried out during the process of fumigation and cleaning.

- Ensure the doors of areas/rooms are properly closed during the fumigation exercise.

- Never operate the fogging machine when the fogger tank is empty.

- Consume freshly prepared solution on the same day. After use, the left over solution should be discarded.

- Keep the direction of the fumigator nozzle in the upward direction before use.

- Wash the hands thoroughly after handling the solution.

- Fumigation should be carried out at the end of the production operation once in a month and whenever required.

Preparation of the Fumigation Agent

- Prepare the fumigation solution (20% Hydrogen Peroxide and 25ppm Silver) as per SOP on preparation of disinfectant solution. See SOP No; BML /QA/093

- Record the details of fumigating solution preparation in annexure 1

| s/no. | Fumigating agent | Fumigant quantity | Purified water (qty) | Final concentration | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1. | Hydrogen peroxide | 400ml | 1600ml | 20v/v | Avoid contact with eyes and skin |

Procedure for Fumigation

- All the equipment, containers, raw/packing materials and power supply panels in the respective area with aluminum film or poly bag.

- Intimate to the Engineering department to close the fresh air damper and exhaust damper completely.

- Switch off the AHU 15minutes before the start of the fumigation.

- Fill in the fogger tank with freshly prepared 20%v/v hydrogen peroxide solution.

- Put on the fogging machine and spray the filling area, mixing area, sterile passages , secondary change room .

- Ensure that proper mist is created in the area, so that the active ingredient is suspended in the atmosphere, thereby giving complete aerial disinfection.

- Keep the area under fumigation for not less than 4 hours or overnight.

- Put the status label “Area under fumigation DO NOT ENTER” at the entry door to production area.

- Follow the above steps for the fumigation of all the areas in the respective units.

- Record the activity in the respective area and equipment usage log book.

Frequency:

- After area shutdown.

- After major civil modification in the area.

- If the microbial count of the area/unit found more than alert limit or as and when required.

MICROBIOLOGICAL PRE- FUMIGATION CHECK

Pre-fumigation Environment Check:

- Expose sterile agar plates of Nutrient Agar (NA) and Sabouraud Dextrose Agar (SDA) 1 each to the air for 15minutes in the area to be fumigated.

- Cover the plates after 15minutes and transfer into the incubator. NA at 370C for 48hours and SDA at 250C for 75hours.

- Count the number of bacteria and fungal colonies.

- Record your observations and write a concise report.

Post-Fumigation Environment Check

- Determine the post-fumigation microbial load to assess the effectiveness of the fumigation by repeating step 1(1-5).

Duration

- Fumigation should be done on monthly basis and preferably during the time when workers are off duty e.g. Saturdays

Safety Precautions:

- Avoid contact with eyes; In case of contact rinse eyes with plenty of water. Always use Protective Clothing, Goggles & Rubber Gloves while using the product.

- REFERENCE AND ENCLOSURE

Annexure 1- Record for preparation of fumigating agent

7.0 TRAINING INVOLVEMENT

| All departmental managers | All sectional heads |
| --- | --- |
| QA Doc. Unit staff | All staff |

8.0 DISTRIBUTION AND CONTROL:

| MASTER COPIES | QUALITY ASSURANCE |
| --- | --- |
| CONTROLLED COPIES | ALL DEPARTMENT |

9.0 CHANGE HISTORY

| CURRENT REVISION | SUPERSEDE | REASON FOR REVIEW |
| --- | --- | --- |
| 00 | Nil | First issue |
| 06 | 05 | - Change in sop format. - Inclusion of traceability of enclosures to parent SOP |

Annexure 1- Record for preparation of fumigating agent

Date:

Fumigating agent:

Quantity of fumigating agent taken:

Quantity of purified water used:

Quantity of fumigating solution prepared:

Prepared by:

Checked by:

Qty. of fumigating solution used:

Qty. of fumigating solution discarded.

Discarded by:

Checked by: