Self-Audit Report

Observations at the Engineering Department

Generally, a good level of adherence to GMP was observed at most of the areas of operations at the engineering department. However, some observations were made during the in-house inspection with majority falling in the category of Minor observations.

The observations would be highlighted under the respective classification headings.

- Critical observations

- WFI storage tank was observed to be washed manually with no evidence of disinfection after such process of washing. Evidence of disinfection or CIP/SIP to be provided

- PVC tank used as feed tank of RO plant. There was no record of leachability at time of inspection.

- No validation record for adequacy of frequency of sanitization RO and DM plant

- Major

- No calibration status on pressure gauges at the RO plant and boiler

- Minor

- Some SOPs were not available at the point of use, especially at Boiler area

- Equipment usage log sheet found at the time of inspection had no portion for supervisor’s check and approval

- Procedure for changing micron filter at the post softener section was not strictly adhered to

- Others

- No evidence of cGMP training at the time of inspection. Though, the evidence was said to be at the QA department.

- The surrounding of the engineering workshop was not well cleaned with cobwebs on the ceilings, floor stained with black oil and office not well arranged.

- The change room was not tidy enough; it needs to be painted.

- The toilet was found very dirty, all wall tiles already turned black and the sinks grossly stained.

- The boiler section was found totally black, probably due to use of black oil. Housekeeping in the area needs to be improved with proper handling of the black oil.

- Several unwanted scraps of defunct equipment were found littering the engineering workshop area

- Defunct equipment in the generator house needed to be covered off with appropriate label affixed

- There was no ETP

- The title of some SOPs appeared too vague

- No cleaner was available for water treatment plant

- The casing of the micron filters at the post softener section should be changed. It has become opaque.

- The heat level at the MCDP/RO plant is too high

- Dead leg was observed on water line